## feedback
Housing Type | Section | Topic | Subtopic | Detail | Classification | Title | Submitted | Submitted By | Comment | Justification/substantiation | Adjudication | Rationale for Decision | Cost increase | Admin Comments
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1e | Depressurization test | April 1, 2013 | Thom Knoll | At 2.0201.1e, Depressurization Test, there appears to be magic with -3 pa which does not seem consistent with other standards of similar extraction. The BPI BA standard lists -3 pa limit only for a natural draft appliance commonly vented with a water heater. A whole table of values exist, including a lower threshold for orphaned water heater. | n/a | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Based on the new BPI 1200, the limit has been deleted
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1e | Depressurization test | October 20, 2014 | Steve Divan | By limiting the depressurization of any combustion zone to -3 pa is in conflict with 2.0299.1a-i. The depressurization limit ranges from -2 to -25 in those sections. Section 2.0201.1e should be changed to allow for differences between appliances detailed in 2.0299.1a-i. | "Depressurization test will include exhaust fans, interior door closure, or duct leakage, or a combination thereof, and will not be more negative than the Manufacturer's certified negative pressure tolerance rating limit when accounting for base pressure" | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1e | Depressurization test | October 31, 2014 | Colorado Energy... | I am confused as what to follow. It states -3 pascals max for depressurization test however 2.0299.1A-I lists depressurization limits for specific appliances. These two specifications appear to be contradictory. | I am confused as what to follow. It states -3 pascals max for depressurization test however 2.0299.1A-I lists depressurization limits for specific appliances. These two specifications appear to be contradictory. | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1e | Depressurization test | March 28, 2014 | DAVID CURTICE | Is this depressurization number for a declared appliance? More information is needed | n/a | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Based on the new BPI 1200, the limit has been deleted
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1e | Depressurization test | March 30, 2015 | Charles Kurnik | Need clarification. | What if it is "more negative"? Should an exhaust fan be turned off? | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): BPI 1200 method now specified
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1e | Depressurization test | April 21, 2014 | Thom Knoll | Prior comment redirect should be 2.0299.1a | n/a | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1e | Depressurization test | April 21, 2014 | Gene Elwood | The -3 pascals is in conflict with depressurization limits in 2.0299.1. | n/a | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1e | Depressurization test | April 14, 2014 | Brad Turner | This specification seems to potentially conflict with the more detailed specifications listed under Section 2.0299.1 - Combustion Appliance Depressurization Tables. 2.0299.1 lists various manufacturer's certified negative pressure tolerance ratings, most of which are more negative than the -3 Pa. limit listed in 2.0201.1e. Suggest language such as, "...and will not be more negative than manufacturer's certified negative pressure tolerance ratings listed in 2.0299.1 depending on appliance type and/or configuration in combustion appliance zone." NOTE - BPI HEP Certification exams (Quality Control Inspector, Energy Auditor, Crew Leader) do require candidates to perform Worst Case CAZ Depressurization tests but DO NOT establish any limits/recommendations based on the appliance type/configuration. Candidate is only required to place CAZ in proper Worst Case scenario and carry out remaining CAZ tests under those conditions. This is confusing for trainers/candidates when the exams are supposed to be based on the SWS. | n/a | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Based on the new BPI 1200, the limit has been deleted
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1e | Depressurization test | April 21, 2014 | Thom Knoll | While this specification lists only -3 pa, at 2.0199.1a is a list of equipment types with differing depressurization limits. Where does the -3 value come from? | n/a | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail 2.0299 has been deleted; -3 value deleted
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1f | Spillage test | April 14, 2014 | Brad Turner | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to identify time limits for spillage, perform spillage tests, and determine if the appliance passes the spillage tests BASED ON BPI STANDARDS (BPI 1200), which are different that the spillage time limits in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and time limits. | n/a | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Aligned with BPI 1200 and NFGC; moved to new specification 2.0201.4a
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1f | Spillage test | August 8, 2014 | Roger Smith | BPI standards | This standard suggests two minutes for spillage, whereas BPI says one minute. Which is correct? | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This item deleted in favor of new specification--2.0201.4a--which has the spillage requirements | no
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1f | Spillage test | April 23, 2014 | Darrel Tenter Tenter | Gasses as used here is misspelled. The plural form of gas is gases. Gasses is the present tense verb. As in "Foam insulation out-gasses". |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1g | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent | April 14, 2014 | Brad Turner | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to measure combustion appliance CO and interpret results BASED ON BPI STANDARDS (BPI 1200), which in some cases are different that the CO thresholds in SWS. BPI Standard 1200 references "ANSI/BSR Z223.1/NFPA 54, National Fuel Gas Code, Table G.6: CO Thresholds", siting CO threshold limits which are different from those listed here in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and threshold limits. | n/a | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Aligned with BPI 1200 and NFGC; moved to new specification 2.0201.4b
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | 2.0201.2a | Outside combustion make-up air | May 15, 2014 | John Krigger | This detail says combustion testing. Is this the place for this standard? Do you mean to require outdoor combustion air duct for every tuned-up appliance? Every replaced appliance? I disagree that this is necessary. It is expensive and has possible unintended consequences. |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): The word "Testing" removed from specification, title now indicates make-up air
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | 2.0201.2b | New appliances | May 15, 2014 | John Krigger | The second paragraph needs to be more specific. |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Added clarifying sentence
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | 2.0201.2d | Gas ovens | April 14, 2014 | Brad Turner | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to measure oven CO and interpret results BASED ON BPI STANDARDS (BPI 1200), which are different than the threshold limits in SWS. BPI Standard 1200 references "ANSI/BSR Z223.1/NFPA 54, National Fuel Gas Code, Table G.6: CO Thresholds", siting an oven CO threshold limit of 225 ppm As Measured, which is different from those thresholds listed here in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and threshold limits. | n/a | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): 225 as-measured now used
Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.3e | Depressurization test | March 30, 2015 | Charles Kurnik | When dealing with combustion byproducts, it seems like the guidance should be consistent. | Most parallel details in the Manufactured Housing version (2.0201.3) do not match the single family version (2.0201.1). It seems like they should. | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Single-family and manufactured housing details are now aligned
Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Air for Natural Draft Appliances | 2.0203.1a | Required combustion air | December 18, 2014 | John Krigger | I think that many agencies interpret this standard as a requirement to install supplemental combustion air, which is usually unnecessary. I have a section in our field guides outlining a procedure to evaluate combustion air with a combustion analyzer. | During worst-case testing, use a combustion analyzer to measure both CO and oxygen (O2).The O2 is an indicator of excess combustion air, and CO may be an indicator of insufficient combustion air. | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Now specifies that combustion air only gets added when necessary to solve spillage issues
Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | 2.0203.2a | Spillage testing | April 23, 2014 | Darrel Tenter Tenter | Comment related to the desired outcome for this detail. Gasses as used here is misspelled. The plural form of gas is gases. Gasses is the present tense verb. As in "Foam insulation out-gasses". |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | 2.0203.2a | Spillage testing | April 21, 2014 | Ted Williams | The two minute threshold is in conflict with the Z21.10.1 design certification standard for safety and is ad hoc. The threshold should be increased to 5 minutes generally or shorter time durations based on additional criteria (e.g., hot vent initial conditions). | n/a | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Two minutes is now only for appliances presumed to be in warm vent condition (furnaces in heating mode, water heaters); five minutes is specified for furnaces not in heating mode
Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Draft Regulation&mdash;Category I Appliance | 2.0203.3a | Assessment | April 23, 2014 | Darrel Tenter Tenter | Comment related to the desired outcome for this detail. Gasses as used here is misspelled. The plural form of gas is gases. Gasses is the present tense verb. As in "Foam insulation out-gasses". |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
Single-Family Homes | Health and Safety | Combustion Safety | Additional Resources | Combustion Appliance Depressurization Limits Table | 2.0299.1a | Atmospheric water heater only (Category I, natural draft), open-combustion appliances | April 21, 2014 | Frank Stanonik | Delete this entire section. There is no recognized test procedure to measure the depressurization resistance of gas and oil-fired appliances so there is no such thing as certified negative pressure tolerance rating. If energy upgrades in an existing home lead to a depressurization issue then the preferred action is not to try to fix the newly created problem but rather to not do the upgrades that created the problem. | n/a | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1a | Assessment | April 21, 2014 | Ted Williams | Minimum requirements from the National Fuel Gas Code (NFGC) Chapter 9, and their extraction into the International Fuel Gas Code (IFGC) and IRC Chapter G24 should be the primary means of addressing the second paragraph and should be so cited. Contrary to previous rejections of comments concerning references to the NFGC coverage, citations of IRC provisions would present the same issues (i.e., applicability to new construction and retrofits requiring code official intervention). More importantly, Section 9.1.24 of the NFGC (2015), which is approved by the ANSI Committee, would apply Chapter 9 to agent work implementing the SWS. Agents implementing the SWS without regard to minimum code would be in violation with this requirement. The serving utility should reexamine providing service to such occupancies. | n/a | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This paragraph has been deleted in deference to spillage testing in new detail 2.0201.4a
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1e | Depressurization test | May 14, 2014 | Darrel Tenter Tenter | The limit of -3 pa conflicts with 2.0299.1 Combustion Appliance Depressurization Limits Table, which shows many CAZ depressurization limits depending on equipment. Suggested change to this language: Depressurization test will include exhaust fans, interior door closure, or duct leakage, or a combination thereof, and will not be more negative than the limits contained in 2.0299.1 Combustion Appliance Depressurization Limits Table. |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | 2.0201.2b | New appliances | September 2, 2014 | John Krigger | I've got the code open and have no idea what this standard is saying. The IRC reference is about clearance. What is this standard requiring? | Too vague. Delete | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Reference to specific section deleted
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | 2.0201.2d | Gas ovens | September 2, 2014 | John Krigger | I'm getting questions about how 200 lines up with 800 in this case when it lines up with 400 in other sections. | 200/400??? | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): The requirement has been aligned with BPI 1200 and the NFGC at 225 ppm as-measured
Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.3g | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent | September 2, 2014 | John Krigger | Here is another 100 ppm number that makes no sense in light of the new 200 ppm initiative. This is sealed combustion equipment after all. | 200/400 if you decide to stick with that standard. | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not only about furnaces, or about sealed combustion; however, the CO limits have been updated
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.1i | Combustion safety testing at completion of retrofitting home | January 7, 2015 | Steve Divan | We recognize the importance of doing a daily test out when a potential hazardous situation exists, but this should only be required when a trained professional identifies a problem. The vast majority of homes do not require testing on this level. To add an additional level of safety, most programs require a CO alarm be installed in every home at the time of the audit and a final test out at the conclusion of the job. Additionally, 2.0201.1i is in conflict with 2.0201.3h which is the manufactured home CAZ testing requirements. 2.0201.3h simply states that a final combustion test must be completed at project completion. This seems to be a more reasonable and appropriate standard for single family homes also. Any standard should consider whether the appliance is sealed combustion, direct vent or even fan assisted, reasonably consider the level of air sealing performed and consider the original tightness of the building. A blanket requirement to test at the end of each work day regardless of conditions and equipment type is costly and unnecessary. | Final combustion testing will be conducted at project completion to ensure compliance with the above specifications | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Many programs do NOT install a CO alarm at audit; the importance of combustion safety makes testing at the end of each day important for the overnight safety of the residents | No, The current SWS will cause costs to rise.The costs associated with training contractors, purchasing the required equipment and paying for contractor or agency staff time to perform these tests would be an unnecessary burden on the WAP program. The potential costs of performing daily testing are significant and have not been shown to be necessary.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | 2.0201.2a | Outside combustion make-up air | September 2, 2014 | John Krigger | I think that this is what the standard means. If not, what does it mean? | For condensing furnaces, install dedicated combustion air pipe directly to the appliance. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This could also be for other appliances. This is make-up air, not direct-vent air
Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.3c | Venting | September 2, 2014 | John Krigger | Mobile homes built since the early to mid seventies have been required to have sealed combustion, meaning that they have no draft regulator. Slope isn't an issue for mobile home furnaces, which vent straight up. | Verify the presence of a sealed-combustion venting system. Verify that the furnace's chimney and combustion-air delivery are properly connected and aren't damaged. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section can apply to older manufactured homes
Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.3e | Depressurization test | September 2, 2014 | John Krigger | CAZ testing is required for open combustion appliances and isn't required for sealed combustion appliances. | When a mobile home furnace is operating, the mobile home must have no open combustion heating devices because of the strong negative pressure created by the furnace. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not about only furnaces or sealed combustion
Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.3e | Depressurization test | September 2, 2014 | John Krigger | Site-built spec applied to mobile home as duplicated in 5.3003 | Change to open combustion from natural draft. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Language is considered appropriate
Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.3e | Depressurization test | September 2, 2014 | John Krigger | Site-built spec applied to mobile home as duplicated in 5.3003 | Change to open combustion from natural draft. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Language is considered appropriate
Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.3f | Spillage test | September 2, 2014 | John Krigger | Again the sealed combustion mobile home appliance shouldn't spill. | No detectable spillage allowed. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not only about furnaces or sealed combustion
Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.3f | Spillage test | September 2, 2014 | John Krigger | If you have an operable furnace and an open-combustion appliance in a mobile, that is unsafe and should be mitigated. Substitute open-combustion for natural draft -- natural draft isn't the problem. | A mobile home furnace should have no detectable spillage because it is sealed combustion. If a mobile home has an open combustion furnace, the home should have both supply and return ducts. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): There are many manufactured homes with natural draft appliances, including water heaters; his section is not just about furnaces, nor about sealed combustion
Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.3f | Spillage test | September 2, 2014 | John Krigger | Spillage at anything but a very small level is unacceptable in a sealed-combustion appliance. Same problems as 5.3003 | 100/200 dilemma. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not about sealed combustion equipment
Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.3g | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent | September 2, 2014 | John Krigger | How do you justify having a higher bar for sealed combustion appliances in mobile homes? | 100/200 dilemma. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not about sealed combustion equipment
Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | 2.0201.3g | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent | September 2, 2014 | John Krigger | Why more stringent for sealed combustion furnaces? | 100/200 dilemma | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not only about furnaces or sealed combustion
Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Draft Regulation&mdash;Category I Appliance | 2.0203.6c | Retesting spillage | December 15, 2015 | Kelly Cutchin C... | Clarify language. | This is about retesting, but is testing for the first time mentioned in this detail? Consider adding a row above this one. Then clarify objective here: Ensure appliance is not spilling longer than 2 minutes with a warm vent. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was deleted because draft regulators only apply for oil-fired appliances and don't belong in the gas-fired section
Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&#173;&mdash;Orphaned Water Heaters | 2.0203.5b | Retesting spillage | December 15, 2015 | Kelly Cutchin C... | Clarify | Objective: Ensure appliance is not spilling longer than 2 minutes with a warm vent. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was combined with 2.0203.2; Spec 2.0203.2c was modified to include new language
Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&#173;&mdash;Orphaned Water Heaters | 2.0203.5a | Spillage testing | December 15, 2015 | Kelly Cutchin C... | Align with BPI 1200 | Spec: If spillage in a combustion appliance with a warm vent exceeds two minutes during pressure testing, specify measures to mitigate. If spillage in a combustion appliance with a cold vent exceeds five minutes during pressure testing, specify measures to mitigate. Objective: Detect excessive spillage of combustion gases. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was combined with 2.0203.2; Spec 2.0203.2a was modified to include new language
Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Air for Natural Draft Appliances | 2.0203.4c | Spillage testing | December 15, 2015 | Kelly Cutchin C... | Align with BPI 1200 | Spec: If spillage in a combustion appliance with a warm vent exceeds two minutes during pressure testing, specify measures to mitigate. If spillage in a combustion appliance with a cold vent exceeds five minutes during pressure testing, specify measures to mitigate. Objective: Detect excessive spillage of combustion gases. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail combined with Detail 2.0203.1; Spec 2.0203.1c was added to include new testing language
Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Draft Regulation&mdash;Category I Appliance | 2.0203.3c | Retesting spillage | December 15, 2015 | Kelly Cutchin C... | Align with BPI 1200 | Where is the first mention of testing spillage in this detail? If this is retesting, the vent will already be warm so the 2 minute limited works. Should there be a row added above that mentions spillage testing with the 2 warm/5 cold vent time limits? | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was deleted because draft regulators only apply for oil-fired appliances and don't belong in the gas-fired section
Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | 5.3003.15i | CO CO Carbon monoxide in flue gas | December 15, 2015 | Kelly Cutchin C... | Align with BPI 1200. Note - This is already in the table of comments to be sent to committee. It should be pulled out and addressed along with the combustion safety updates. | CO in the undiluted flue gas will be less than 400 ppm air free. | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): The document has been updated to "400 ppm air-free" to align with BPI 1200. In addition, this same language was updated in 5.3003.14e, for both single family and manufactured housing.