## General Comments
Submitted | Updated | Classification | Comment | Adjudication | Rationale for Decision | Recommended New Text
April 21, 2014 | April 21, 2014 | General Comment | I’ve found the SWS commenting easy to use and I’ve submitted quite a few comments. I like the fact that I can review my previous comments to avoid submitting the same comment twice. I realize that today is the last day for comments in the current round. I have a few general comments and suggestions that don’t really fit within the commenting tool. • Detail names and subtopics should be more descriptive and specific. I have difficulty knowing what’s inside the detail and subtopic by their current names. • I suggest using the find-and-replace function to change all wills to musts. • What specifically triggers a requirement to comply with a detail? Is there a way to make this clearer? There may be a number of potential triggers that would require compliance with a detail. 1. An agency chooses a cost-effective measure, covered by the SWS, and plans to install it. 2. A cost-effective measure needs an associated repair measure for durability. 3. A condition at the home requires a mitigation procedure to accompany weatherization for health, safety, and/or durability. 4. A measure may be required if not currently present in a home. If these triggers or others are relevant, could you state them at the detail level for the sake of clarity? There are two terms that could cause confusion: ventilation and venting. Could we use venting for combustion appliances, and use ventilation for air movement to control moisture, pollutants, and accumulated heat? Thanks for the opportunity to comment. | Accepted with Modification | At this time, the wills will not be changed to musts. The committee agrees about the confusion with ventilation versus venting. Venting should be used for combustion appliances, and ventilation should be used for air movement to control moisture, pollutants, and accumulated heat. Further investigation is required to understand the extent of the changes to the SWS.
April 14, 2014 | April 14, 2014 | General Comment | I wish to comment on the issue of draft testing (or lack thereof) in the SWS. Since there is no specification regarding performing draft testing within the SWS, I am unable to comment using the comment tool, so I am addressing the comment to the general mailbox. I wish to point out that the SWS does not include any specification on performing a draft test on combustion appliances. However, on the BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) candidates are required calculate minimum draft pressure based on existing weather conditions, perform worst case draft testing on DHW, and make appropriate recommendations BASED ON BPI STANDARDS. Because these BPI HEP exams are supposed to be based on the SWS, this is confusing for trainers/candidates. To further confuse matters, BPI 1200, also does not include any information regarding calculating minimum draft pressures and/or performing draft testing; the BPI Standard containing this information is in the BPI Building Analyst Professional Standard. I realize the BPI Standards and exams are not under the control of the SWS Committees, but this area of conflict and confusion should be noted and somehow addressed among the organizations’ working groups/committees. | Further Investigation Required | Currently there are discussions in the industry around combustion appliance zone testing. BPI 1200 is currently undergoing revision, and the issues addressed in this comment should be worked out when revision is complete. When the issue is resolved, the SWS will be updated.
April 21, 2014 | April 21, 2014 | General Comment | I have had difficulty understanding how particular work scopes related to each housing type were selected. As a cross-cutting exercise it would seem appropriate to review the three types side by side and, where possible, to standardize wherever possible. For example, at 3.11 Walls, within Air Sealing, provides specific instructions for only MH (3.1101.1) and MF (3.1101.2), but nothing for single family, though the instructions for MH seem sage advice. Another cross-cut that seems to have failed is between the various sections, including air sealing, insulation, and heating and cooling, reiterating the requirement to check CAZ safety offered at 2.0201.1i. (Also note no subsection h.) There is a requirement at job completion to test out CAZ safety, but nothing regarding potential changes during multi-day, or multi-contractor, projects which could impact CAZ safety. | Further Investigation Required | It was agreed that a crosscutting review is important. DOE and NREL will plan to complete this if possible. New search functionality and the application programming interface-generated spreadsheet would be helpful in assisting with this review.
April 21, 2014 | April 21, 2014 | General Comment | The term of Cathedral ceiling with the definition of 'A condition in which the ceiling has the same slope as the roof' received the following comment:See Vaulted Ceiling | Rejected | Two different definitions.
April 21, 2014 | April 21, 2014 | General Comment | The term of Closed crawl space with the definition of 'A foundation without wall vents that uses air-sealed walls, ground and foundation moisture control, and mechanical drying methods to control crawl space moisture; Insulation may be located at the conditioned floor level or on the exterior walls; Return pathways are not allowed from the crawl space to the living space' received the following comment:Ducted returns, or air barrier exists between crawl space and conditioned space? | Rejected | No suggested change.
April 21, 2014 | April 21, 2014 | General Comment | The term of Ignition barrier with the definition of 'Any layer of material that protects another from catching fire due to heat or spark' received the following comment:Specifically provide that intumescent paint can be an option for ignition barrier, e.g., paint B vent as an alternative to building sheet metal dam. | Rejected | Comment covers detail, where the definition is intended to be broad.
April 21, 2014 | April 21, 2014 | General Comment | The term of Interior storm window with the definition of 'An additional window assembly installed on the interior of the main window' received the following comment:It would be nice to avoid "storm" for this product. An interior window thermal product could be operable like a storm, an insulating product such as insulating shade, or multi-glazing such as glazing attached to or replacing existing sash. A real terminology conundrum! | Rejected | using generally accepted nomenclature for the definitions. Comment. No question.
April 21, 2014 | April 21, 2014 | General Comment | The term of JTA with the definition of 'Job Task Analysis' received the following comment:As applied, JTA is more often "learning objectives" of instruction, and in reality does not involve analysis. | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
April 21, 2014 | April 21, 2014 | General Comment | The term of Knee wall with the definition of 'Any wall between the conditioned space and the attic' received the following comment:This definition could lead to confusion if applied to the wall common between finished attic and a contiguous UNFINISHED attic space (e.g., partially finished attic). | Rejected | Using a common industry-accepted term here.
April 21, 2014 | April 21, 2014 | General Comment | The term of RPA with the definition of 'Radiant Professional Alliance' received the following comment:Changed name from Radiant Panel Association | Accepted with modification | This is the current name.
April 21, 2014 | April 21, 2014 | General Comment | The term of Standby loss with the definition of 'Heat loss through the outer part of a water heater; Energy that is used even when a device is turned off' received the following comment:Standby loss may have more general meaning, and include loss to the vent (an inner part of tank heaters!) when burner is off. Would the term include "off cycle" loss from hydronic equipment? | Rejected | Accurate in context.
April 21, 2014 | April 21, 2014 | General Comment | The term of Vapor barrier with the definition of 'A material that retards the passage of water vapor and contains a perm rating of less than 1' received the following comment:A material that slows the passage of water vapor and contains a perm rating according to the current version of ASTM standard on vapor retarder | Accepted with Modification | The definition of vapor barrier will be removed.
April 21, 2014 | April 21, 2014 | General Comment | The term of Vapor retarder with the definition of 'A material that slows the passage of water vapor and contains a perm rating above 1' received the following comment:A material that slows the passage of water vapor and contains a perm rating according to the current version of ASTM standard on vapor retarder | Accepted with Modification | Vapor retarder will be defined as "A material or construction that impedes the transmission of water vapor under specified conditions" per ASTM E1745 | A material or construction that impedes the transmission of water vapor under specified conditions
April 21, 2014 | April 21, 2014 | General Comment | The term of Wind intrusion with the definition of 'A condition where air from outside of a structure can pass through insulation and reduce its performance' received the following comment:Perhaps air intrusion would be better, since pressure driving air through insulation could also result from stack or induced forces. | Accepted

## Specification Comments
Housing Type | Section | Topic | Subtopic | Detail | Title | Submitted | Updated | Classification | Comment | Adjudication | Rationale for Decision | Recommended New Text
Single-Family Homes | Health and Safety | Safe Work Practices | Safe Work Practices | Global Worker Safety | Carbon monoxide ( CO CO Carbon monoxide ) | March 18, 2014 | March 18, 2014 | 2.0100.1e | Carbon monoxide alarms should be present or installed in all homes with combustion appliances. | Rejected | Attached garages, unvented portable space heaters, and other equipment such as portable generators, are sources that may exist and contribute CO to any home.
Single-Family Homes | Health and Safety | Safe Work Practices | Safe Work Practices | Global Worker Safety | Power tool safety | April 4, 2014 | April 4, 2014 | 2.0100.1h | What about properly working safety guards? | Accepted |  | Power tools will be inspected and used in accordance with manufacturer specifications and OSHA regulations to eliminate hazards such as those associated with missing ground prongs, ungrounded circuits, misuse of power tools, safety guards, noise, and improper or defective cords or extension cords All devices used will be verified as GFCI protected or double insulated Exhaust gases from compressors and generators will be prevented from entering interior space
Manufactured Housing | Health and Safety | Safe Work Practices | Safe Work Practices | Global Worker Safety | Prevention through design | March 11, 2014 | March 11, 2014 | 2.0100.2a | Example | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Health and Safety | Safe Work Practices | Heating and Cooling Equipment | Combustion Worker Safety | Carbon monoxide ( CO CO Carbon monoxide ) | March 11, 2014 | March 11, 2014 | 2.0105.1b | 9 ppms in home WAP Standards, not BPI | Rejected | There is not a national WAP standard that contains 9ppm. Additionally, 35ppm is an EPA 1-hour averaged value (as opposed to an 8-hour averaged value).
Single-Family Homes | Health and Safety | Safe Work Practices | Heating and Cooling Equipment | Heating and Cooling Worker Safety | Mercury | April 21, 2014 | April 21, 2014 | 2.0105.2b | Should we be removing all mercury containing thermostats and replacing them regardless if we are doing HVAC work in the home? | Accepted |  | When replacing existing thermostats, identify and dispose of any mercury containing thermostats in accordance with Environmental Protection Agency (EPA) guidance
Single-Family Homes | Health and Safety | Safe Work Practices | Heating and Cooling Equipment | Heating and Cooling Worker Safety | Mercury | April 21, 2014 | April 21, 2014 | 2.0105.2b | The goal is to protect workers and occupants from Hg exposure. I recommend that if we are replacing a mercury thermostat we dispose of the old one according to EPA guidance, BUT if there is a functional Hg thermostat in place, I recommend we leave it there, as removing and transporting it will have a much higher risk of breakage or leakage than simply leaving it in place. This coupled with client education about mercury will be much more cost effective than simply removing it because of a potential hazard. Are we also going to remove the Hg "silent" wall switches?, or the mercury switches used in autos until 2004? | Accepted |  | When replacing existing thermostats, identify and dispose of any mercury containing thermostats in accordance with Environmental Protection Agency (EPA) guidance
Single-Family Homes | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Crawl Spaces&mdash;Pre-Work Qualifications | Appliance and heating, ventilation, and air conditioning ( HVAC HVAC Heating, ventilation, and air conditioning ) system repairs and change outs | April 21, 2014 | April 21, 2014 | 2.0111.2g | What is the intent with this? What portion of the IRC applies? Please provide more detailed references. | Accepted with Modifications | The SWS refers to code only and not a specific section. Additional langugage will be generated for the linked "IRC". | Crawl space upgrades (e.g., sealing and insulation) are to be undertaken after appliance and HVAC system work has been completed and inspected in accordance with the 2012 IRC and/or the authority having jurisdiction
Single-Family Homes | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Crawl Spaces&mdash;Debris Removal | Debris removal | April 18, 2014 | April 18, 2014 | 2.0111.3a | Suggested language: Under-floor grade will be removed of all vegetation and organic material, unnecessary material, and debris greater than 1" will be removed from within 3 feet of the crawl space access and in any areas likely to be trafficked for appliance servicing. The current language, which requires all debris greater than 1" to be removed from the entire crawl space, is extremely expensive and time-consuming, often not practical, and not necessary to achieve the stated objectives. Only certain areas of the crawl space are likely to experience human traffic, specifically in the area around the crawl space access, the area around any appliances that need maintenance (e.g. furnace located in the crawl space), and between those two areas. Other means of meeting the stated objectives could also be included, such as putting a double layer of ground cover in those specific areas or putting roofing or other durable material on top of the ground cover in those areas. Any of these would be reasonable, and the rest of the crawl space could be left as is (i.e. no significant debris removal necessary). | Accepted with Modifications | The intent of the comment was met with alternate text. | Under-floor grade will be removed of all vegetation and organic material. , unnecessary material, Debris that can cause injury or puncture ground covers (e.g., nails, glass, sheet metal screws, etc) will be removed from the crawl space
Single-Family Homes | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Negative Pressure Contamination Control | Interior sealing | April 21, 2014 | April 21, 2014 | 2.0111.4b | If the crawl space is within the thermal and pressure boundaries of the building, there is no reason to automatically seal all penetrations, without an IAQ problem in the crawl space. This will increase the likelihood of frozen pipes in cold weather. | Accepted with Modifications |  | New text for 4c: [renumber this spec to "a"] A negative pressure will be maintained in the crawl space with reference to the house while work is being peformed in the crawl space [In addition, delete the current a, and b specs]
Single-Family Homes | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Negative Pressure Contamination Control | Pressure | March 31, 2014 | March 31, 2014 | 2.0111.4c | People, including me, are confused by this spec. If you seal the foundation vents, where is the make-up air for the fan gonna come from? I don't quite see the point of this spec. | Accepted with Modifications |  | New text for 4c: [renumber this spec to "a"] A negative pressure will be maintained in the crawl space with reference to the house while work is being peformed in the crawl space [In addition, delete the current a, and b specs]
Manufactured Housing | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Prework Qualifications (Home Installation) | Installation deficiencies | March 28, 2014 | March 28, 2014 | 2.0111.5a | What in the world does this have to do with energy conservation. We are not building inspectors nor do we have the time to investigate this depth of detail for each project. | Accepted |  | Any installation deficiencies that may affect worker safety or integrity or installed measures will be repaired before starting work
Manufactured Housing | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Prework Qualifications (Home Installation) | Stabilization | March 28, 2014 | March 28, 2014 | 2.0111.5b | How do we pay for this with energy conservation as the goal? | Rejected | It is often necessary to defer the house or complete non-energy measures to ensure the inegrity of the energy measures in the house.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Assessment | April 21, 2014 | April 21, 2014 | 2.0201.1a | Minimum requirements from the National Fuel Gas Code (NFGC) Chapter 9, and their extraction into the International Fuel Gas Code (IFGC) and IRC Chapter G24 should be the primary means of addressing the second paragraph and should be so cited. Contrary to previous rejections of comments concerning references to the NFGC coverage, citations of IRC provisions would present the same issues (i.e., applicability to new construction and retrofits requiring code official intervention). More importantly, Section 9.1.24 of the NFGC (2015), which is approved by the ANSI Committee, would apply Chapter 9 to agent work implementing the SWS. Agents implementing the SWS without regard to minimum code would be in violation with this requirement. The serving utility should reexamine providing service to such occupancies. | Further Investigation Required | Currently there are discussions in the industry around CAZ testing. When the issue is resolved, the SWS will be updated.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Fuel leak detection | April 21, 2014 | April 21, 2014 | 2.0201.1b | This is unnecessary. Unless there is some other indication of a potential gas leak, there is no need to test gas connections that have been undisturbed. | Rejected | It cannot be confirmed that the gas connection was undisturbed; therefore , the SWS will continue to recommend testing for fuel leak.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Venting | April 21, 2014 | April 21, 2014 | 2.0201.1c | What is the regulator identified in the Objectives? For most residential gas fired appliances the only regulator on the equipment is the gas pressure regulator which ha snothing to do with th event system. Many gas appliances have draft hoods; few have draft regulators. Modify to use correct terminlogy consistent with euipment safety standards and installation codes. | Accepted |  | Objective should state: Determine if a draft regulator is present and working and if vent system is in good condition and installed properly
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Venting | April 1, 2013 | March 12, 2014 | 2.0201.1c | The requirements in 2.0201.1c, units outside each sleeping area, seem inappropriate for CO detection; appropriate instead for smoke alarms. ASHRAE 62.2 - 2010, addendum l (that's an L) adds paragraph 6.9 to the standard which requires only one Carbon Monoxide detector per dwelling unit. | Rejected | The comment does not apply to the section where comment was submitted.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test | April 21, 2014 | April 21, 2014 | 2.0201.1e | Prior comment redirect should be 2.0299.1a | Further Investigation Required | Currently there are discussions in the industry around CAZ testing. When the issue is resolved, the SWS will be updated.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test | April 21, 2014 | April 21, 2014 | 2.0201.1e | While this specification lists only -3 pa, at 2.0199.1a is a list of equipment types with differing depressurization limits. Where does the -3 value come from? | Further Investigation Required | Currently there are discussions in the industry around CAZ testing. When the issue is resolved, the SWS will be updated.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test | April 21, 2014 | April 21, 2014 | 2.0201.1e | The -3 pascals is in conflict with depressurization limits in 2.0299.1. | Further Investigation Required | Currently there are discussions in the industry around CAZ testing. When the issue is resolved, the SWS will be updated.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test | April 14, 2014 | April 14, 2014 | 2.0201.1e | This specification seems to potentially conflict with the more detailed specifications listed under Section 2.0299.1 - Combustion Appliance Depressurization Tables. 2.0299.1 lists various manufacturer's certified negative pressure tolerance ratings, most of which are more negative than the -3 Pa. limit listed in 2.0201.1e. Suggest language such as, "...and will not be more negative than manufacturer's certified negative pressure tolerance ratings listed in 2.0299.1 depending on appliance type and/or configuration in combustion appliance zone." NOTE - BPI HEP Certification exams (Quality Control Inspector, Energy Auditor, Crew Leader) do require candidates to perform Worst Case CAZ Depressurization tests but DO NOT establish any limits/recommendations based on the appliance type/configuration. Candidate is only required to place CAZ in proper Worst Case scenario and carry out remaining CAZ tests under those conditions. This is confusing for trainers/candidates when the exams are supposed to be based on the SWS. | Further Investigation Required | Currently there are discussions in the industry around CAZ testing. When the issue is resolved, the SWS will be updated.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test | March 28, 2014 | March 28, 2014 | 2.0201.1e | Is this depressurization number for a declared appliance? More information is needed | Further Investigation Required | Currently there are discussions in the industry around CAZ testing. When the issue is resolved, the SWS will be updated.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test | April 1, 2013 | March 12, 2014 | 2.0201.1e | At 2.0201.1e, Depressurization Test, there appears to be magic with -3 pa which does not seem consistent with other standards of similar extraction. The BPI BA standard lists -3 pa limit only for a natural draft appliance commonly vented with a water heater. A whole table of values exist, including a lower threshold for orphaned water heater. | Further Investigation Required | Currently there are discussions in the industry around CAZ testing. When the issue is resolved, the SWS will be updated.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test | April 21, 2014 | April 21, 2014 | 2.0201.1e | It is neither appropriate nor always necessary to conduct a Combustion Appliance Zone (CAZ) test. The implication that the CAZ test provides accurate information about the appliances safe operation is wrong. The CAZ test only evaluates the relationship of the house's ventilation process and the appliance's vent system. It does not in any way check other aspects of the safe operation of the appliance. If a gas appliance has been installed in accordance with the National Fuel Gas Code then depressurization should not be an issue because an adequate supply of combustion and ventilation air will be provided to the appliance. If an energy upgrade to an existing home changes the situation of the appliance such that the installation may no longer be in accordance with the National Fuel Gas Code, then that upgrade should not be implemented or be removed. Furthermore, the test is insufficient in that it only looks at depressurization, which may be an issue only when the appliance is installed in the conditioned space. There are other safety issues that may develop due to the installation of energy retrofit measures. We suggest the following to replace the specification in all cases where the BPI CAZ depressurization test is mentioned: The venting of the combustion equipment, the adequacy of the venting system and the potential for spillage shall be evaluated using a procedure specified in a nationally-recognized, consensus developed equipment safety standard or installation code or other procedure acceptable to the authority having jurisdiction. | Rejected | There are many situations where appliances may have been installed before codes, or in jurisdictions where there are no building codes.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test | April 14, 2014 | April 14, 2014 | 2.0201.1f | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to identify time limits for spillage, perform spillage tests, and determine if the appliance passes the spillage tests BASED ON BPI STANDARDS (BPI 1200), which are different that the spillage time limits in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and time limits. | Further Investigation Required
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent | April 14, 2014 | April 14, 2014 | 2.0201.1g | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to measure combustion appliance CO and interpret results BASED ON BPI STANDARDS (BPI 1200), which in some cases are different that the CO thresholds in SWS. BPI Standard 1200 references "ANSI/BSR Z223.1/NFPA 54, National Fuel Gas Code, Table G.6: CO Thresholds", siting CO threshold limits which are different from those listed here in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and threshold limits. | Further Investigation Required
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Combustion safety testing at completion of retrofitting home | April 8, 2014 | April 8, 2014 | 2.0201.1i | While it is a great idea to do a final combustion safety test. For occupant and worker safety there should be a test for all envelope changing measures upon completion of those measures or at the end of the work day in which the envelope measures were implemented. | Accepted |  | At the conclusion of each work day in which envelope or duct sealing measures have been performed, depressurization and spillage testing will be performed.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Outside combustion make-up air | April 21, 2014 | April 21, 2014 | 2.0201.2a | This is unnecessarily restrictive. It should be deleted. Fuel fired equipment should be installed in accordance with the applicable installation code. That will assure an adequate supply of combustion air. There are millions of gas fired appliances installed in residences that use indoor air for combustion and which are not putting any products of combustion into the residence. | Accepted with Modifications | Outside air must be brought in to provide makeup air, so the detail cannot be removed. The detail was modified to include "Where applicable" to address the comment. | Where applicable, combustion air will be provided from the outside and installed in accordance with the 2012 IRC for the type of appliance present
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Outside combustion make-up air | April 21, 2014 | April 21, 2014 | 2.0201.2a | The requirements for outside combustion air for all combustion appliance is in conflict with the National Fuel Gas Code (NFGC) Chapter 9 and the International Fuel Gas Code and IRC, both of which extract the coverage of combustion air from the NFGC. Contrary to previous rejections of comments concerning references to the NFGC coverage, citations of IRC provisions would present the same issues (i.e., applicability to new construction and retrofits requiring code official intervention). More importantly, Section 9.1.24 of the NFGC (2015), which is approved by the ANSI Committee, would apply Chapter 9 to agent work implementing the SWS. | Accepted with Modifications | Outside air must be brought in to provide makeup air, so the detail cannot be removed. The detail was modified to include "Where applicable" to address the comment. | Where applicable, combustion air will be provided from the outside and installed in accordance with the 2012 IRC for the type of appliance present
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | New appliances | April 21, 2014 | April 21, 2014 | 2.0201.2b | Requirements for direct vent and so-called "sealed combustion" appliances would disallow high-efficiency condensing combustion appliances. Such appliances, installed in accordance with Chapter 9 of the NFGC and IRC Section G2407 combustion air requirements, have never been shown to generate hazardous conditions. This technologically-prescriptive language should be eliminated. | Accepted with Modifications | The SWS is not prescriptive. The document describes the outcome, rather than how to complete it. | New appliance will be installed in accordance with manufacturer specifications, 2012 IRC G2427.8, and additional applicable codes Replacement equipment venting will be assessed to ensure other existing equipment is not adversely affected
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | New appliances | April 21, 2014 | April 21, 2014 | 2.0201.2b | If replacing "appliances" direct-vent will be installed. Water heaters are appliances and in 7.8102.1a it requires direct vented or power vented water heaters. Is this a contradiction? | Accepted with Modifications | The SWS is not prescriptive. The document describes the outcome, rather than how to complete it. | New appliance will be installed in accordance with manufacturer specifications, 2012 IRC G2427.8, and additional applicable codes Replacement equipment venting will be assessed to ensure other existing equipment is not adversely affected
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | New appliances | April 21, 2014 | April 21, 2014 | 2.0201.2b | This is unnecessarily restrictive and should be deleted. See my previous comment. | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | New appliances | March 28, 2014 | March 28, 2014 | 2.0201.2b | Does this requirement apply to all gas applainces in all cases? | Rejected | Yes, the specification applies to all gas appliances in all cases.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | CO CO Carbon monoxide detection and warning equipment | April 21, 2014 | April 21, 2014 | 2.0201.2c | Replace the reference to ASHRAE 62.2 with a reference to the appropriate NFPA standard which covers the installation of CO alarms in residences. | Rejected | The citation of ASHRAE 62.2 states that CO detectors should be in all homes. ASHRAE 62.2 references NFPA 720 for the location of the CO detector.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | CO CO Carbon monoxide detection and warning equipment | April 21, 2014 | April 21, 2014 | 2.0201.2c | As a member of the ASHRAE Standard 62.2 Committee, I can tell you that that standard is not the appropriate reference standard. The standard citation for this coverage should be NFPA 720. More applicable, however, the minimum code requirement for the coverage, IRC Section R315, should be cited since it is the dominant enforceable code. | Rejected | The citation of ASHRAE 62.2 states that CO detectors should be in all homes. ASHRAE 62.2 references NFPA 720 for the location of the CO detector.
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Gas ovens | April 14, 2014 | April 14, 2014 | 2.0201.2d | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to measure oven CO and interpret results BASED ON BPI STANDARDS (BPI 1200), which are different than the threshold limits in SWS. BPI Standard 1200 references "ANSI/BSR Z223.1/NFPA 54, National Fuel Gas Code, Table G.6: CO Thresholds", siting an oven CO threshold limit of 225 ppm As Measured, which is different from those thresholds listed here in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and threshold limits. | Further Investigation Required
Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Solid fuel burning appliances | March 28, 2014 | March 28, 2014 | 2.0201.2f | Does mean that all existing solid fuel appliances MUST be replaced if they do not meet this spec? | Accepted |  | If the solid fuel burning appliance is the primary heat source and has signs of structural failure replace solid fuel burning appliance with UL-listed and EPA - certified appliances if the existing appliance is not UL-listed
Single-Family Homes | Health and Safety | Combustion Safety | Unvented Space Heaters | Unvented Space Heaters: Propane, Natural Gas, and Kerosene Heaters | Removal | April 21, 2014 | April 21, 2014 | 2.0202.1a | Section 2: Health & Safety, states that all replacement combustion appliances WILL be direct vent or sealed combustion. In Section 7: Baseload, notation 7.8102.1a Water Heater Selection; parameters are given for choosing a replacement. Are sealed or direct vent combustion appliances mandatory in all replacement scenarios? And have issues concerning the practicality of this requirement been taken into account, e.g., customer’s financial ability to service higher end units, housing type conflicts, etc? | Rejected | The comment does not apply to the section where comment was submitted. An unvented combustion appliance cannot be installed.
Single-Family Homes | Health and Safety | Combustion Safety | Unvented Space Heaters | Unvented Space Heaters: Propane, Natural Gas, and Kerosene Heaters | Removal | April 21, 2014 | April 21, 2014 | 2.0202.1a | The recommendation concerning the removal of unvented space heaters is unfounded insofar as it applies to gas-fired vent free heaters and fireplaces. There is no rational justification for removing a properly installed and properly operating gas-fired vent free heater or fireplace. If there is a problem with the installation or operation it should be repaired, if possible. The only situation where a suggestion to remove the unit would be appropriate is in the case where the existing gas-fired vent-free appliance is so old that it does not incorporate an Oxygen Depletion Sensing (ODS) safety system. In that case the recommendation should be to replace the unit with a new gas-fired vent-free appliance complying with the Z21.11.2 safety standard. Also, equipment in the field is not used in conformance with any equipment safety standard. The equipment safety standard cannot address how consumer’s use equipment. This specification should address education about proper us eof gas-fired unvented space heaters. | Rejected | Studies have shown that NO2 levels frequently exceed EPA standards.
Single-Family Homes | Health and Safety | Combustion Safety | Unvented Space Heaters | Unvented Space Heaters: Propane, Natural Gas, and Kerosene Heaters | Removal | April 21, 2014 | April 21, 2014 | 2.0202.1a | The second paragraph is erroneous since the Z21.11.2 does not cover field operation of the covered products. A better approach would be for the investigator to verify that the covered product is sized in compliance with Z21.11.2 (input to room volume), which is covered by the standard currently. Claims of operating hazards covered in the third paragraph are not technically supported. In fact, the action called for, and the section overall, misses a critical safety issue and opportunity for agent intervention: verifying that the Z21.11.2 product carries an oxygen depletion sensor (ODS) as required by the current edition of the standard, and for products that do not, requiring their direct replacement with a unit that is so equipped. According to documentation from the U. S. Consumer Product Safety Commission (CPSC), no deaths due to carbon monoxide (CO) have been attributed to unvented space heaters with installed ODS systems. | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Health and Safety | Combustion Safety | Unvented Space Heaters | Unvented Space Heaters: Propane, Natural Gas, and Kerosene Heaters | Occupant education | April 21, 2014 | April 21, 2014 | 2.0202.1b | No consensus-based and standardized education has been identified for use in educating occupants regarding unvented combustion appliances, whether for unvented space heaters or cooking appliances. This text should be replaced with a recommendation to contact the local health department to receive public health information implemented within the jurisdiction of the installation. | Rejected | The judgement as to what educational materials should be used is being left to the implementer.
Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | Spillage testing | April 21, 2014 | April 21, 2014 | 2.0203.2a | The two minute threshold is in conflict with the Z21.10.1 design certification standard for safety and is ad hoc. The threshold should be increased to 5 minutes generally or shorter time durations based on additional criteria (e.g., hot vent initial conditions). | Further Investigation Required | Currently there are discussions in the industry around CAZ testing. When the issue is resolved, the SWS will be updated.
Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | Flue gas removal (chimney liner or approved methods) | March 28, 2014 | March 28, 2014 | 2.0203.2b | Does this apply to existing appliances | Rejected | This specification of the SWS applies to existing appliances.
Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | Retesting spillage | April 21, 2014 | April 21, 2014 | 2.0203.2c | See my comment on 2.0203.2a, which applies here as well. | Further Investigation Required | Currently there are discussions in the industry around CAZ testing. When the issue is resolved, the SWS will be updated.
Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | Occupant health and safety | March 28, 2014 | March 28, 2014 | 2.0203.2f | What sensitivity of alarm is required? digital read out? event tracking? | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Draft Regulation&mdash;Category I Appliance | Installation (if action is required) | March 28, 2014 | March 28, 2014 | 2.0203.3b | I have never heard of a draft regulator on a gas fired appliance. Please clarify | Accepted with Modifications | "Draft regulator" was added to the glossary.
Multifamily Homes | Health and Safety | Combustion Safety | Gas and Oil-Fired Equipment | Gas and Oil-Fired Equipment | Orphaned equipment Orphaned equipment Condition when one smaller combustion appliance exists after being commonly vented with a larger appliance. What remains is a larger exhaust flue or chimney than is necessary for the remaining smaller appliance | March 24, 2014 | March 24, 2014 | 2.0205.1c | One gas furnace in a units and both the hot water heater and gas furnace in the community room were not venting correctly. At the time these units are serviced proper venting of combustion gases must be verified. | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Health and Safety | Combustion Safety | Additional Resources | Combustion Appliance Depressurization Limits Table | Atmospheric water heater only (Category I, natural draft), open-combustion appliances | April 21, 2014 | April 21, 2014 | 2.0299.1a | Delete this entire section. There is no recognized test procedure to measure the depressurization resistance of gas and oil-fired appliances so there is no such thing as certified negative pressure tolerance rating. If energy upgrades in an existing home lead to a depressurization issue then the preferred action is not to try to fix the newly created problem but rather to not do the upgrades that created the problem. | Further Investigation Required | Currently there are discussions in the industry around CAZ testing. When the issue is resolved, the SWS will be updated.
Single-Family Homes | Health and Safety | Safety Devices | Combustion Safety Devices | Carbon Monoxide Alarm or Monitor | CO CO Carbon monoxide detection and warning equipment (hardwired) | April 21, 2014 | April 21, 2014 | 2.0301.2a | ASHRAE 62.2 is an improper citation. IRC R315 should be cited. | Rejected | The citation of ASHRAE 62.2 states that CO detectors should be in all homes. ASHRAE 62.2 references NFPA 720 for the location of the CO detector.
Single-Family Homes | Health and Safety | Safety Devices | Combustion Safety Devices | Carbon Monoxide Alarm or Monitor | CO CO Carbon monoxide detection and warning equipment (battery operated) | April 21, 2014 | April 21, 2014 | 2.0301.2b | ASHRAE 62.2 is an improper citation. IRC R315 should be cited. | Rejected | The citation of ASHRAE 62.2 states that CO detectors should be in all homes. ASHRAE 62.2 references NFPA 720 for the location of the CO detector.
Single-Family Homes | Health and Safety | Moisture | Air Sealing | Air Sealing Moisture Precautions | Moisture precautions for crawl spaces | April 10, 2014 | April 10, 2014 | 2.0401.1b | There is a typo in your thickness for ground cover. The proper thickness for ground cover is 6 mil, not 6 millimeters. | Accepted |  | Exposed earth will be covered with a continuous, durable, sealed Class 1 vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 a minimum of 6 mils in thickness
Single-Family Homes | Health and Safety | Moisture | Air Sealing | Air Sealing Moisture Precautions | Moisture precautions for crawl spaces | April 8, 2014 | April 8, 2014 | 2.0401.1b | Typo for minimum thickness (6 mil) | Accepted |  | Exposed earth will be covered with a continuous, durable, sealed Class 1 vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 a minimum of 6 mils in thickness
Single-Family Homes | Health and Safety | Moisture | Air Sealing | Vented Crawl Space&mdash;Venting | Venting | April 21, 2014 | April 21, 2014 | 2.0401.2a | Given the level of detail shown in "space conditioning" it seems like you need more detail here. Suggest at least the 1/1500 passive ventilation openings when the crawl space has a vapor barrier, which is required, right? A lot of crawl spaces without obvious problems meet this standard already if we install a ground moisture barrier. The 2012 IRC section number is R408.1. | Accepted with Modifications | The code should take precedence in this case. Authorities having jurisdication may have more expansive rules. State or local program may have their own rule. | Venting will be performed in accordance with the 2012 IRC or the authority having jurisdiction
Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Vented Crawl Spaces&mdash;Ground Moisture Barrier | Scheduling | April 21, 2014 | April 21, 2014 | 2.0403.1a | You say the GMB will be installed last. What does this mean? Do you mean that if you insulate the foundation walls or floor that the GMB is required and that you want it installed last to protect it from the traffic necessitated by the insulation installation? Maybe I'm just missing something here, but seems like some additional information is necessary. I think many readers are confused by language like this. There seems to be some requirements, but when are the requirements triggered? Do we install a GMB universally? Are we required to install a GMB when we insulate? when there's a problem? If one weatherization measure triggers a repair or another measure, please call that out. | Accepted with Modifications | The detail was editted to be outcome based rather than processed base; therefore, the title of "Scheduling" was changed to "Material integrity". | Change Spec to: Title: Material integrity Specification: Care will be taken to prevent punctures during installation Ojective: Protect ground moisture barrier from damage during other crawl space work
Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Vented Crawl Spaces&mdash;Ground Moisture Barrier | Material specification | April 18, 2014 | April 18, 2014 | 2.0403.1c | ASTM D703 has been withdrawn. It was replaced with D4549. However, the industry accepted test method for vapor retarders is ASTM E1745. Class A offers the best puncture resistance (2200g and Class B at 1700g) as tested in accordance wtih ASTM D1709. | Accepted with Modifications | The new text provides more detail and allows for the most recent ASTM standard. | A ground moisture barrier with a rating of no more than 0.1 perm will be used A minimum expected service life of 10 years will be ensured A ground moisture barrier will be used that meets tear and puncture resistance of 6 mil or the current ASTM standard for puncture and tear resistance
Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Vented Crawl Spaces&mdash;Ground Moisture Barrier | Overlap seams | March 31, 2014 | March 31, 2014 | 2.0403.1d | I would prefer that you require sealing the seams. Many times I've seen mold growing on the overlap without seam sealing. There is a lot of air leakage through the ground in rocky soil, including Radon. Why not reduce air leakage and Radon with a small additional effort of sealing the seams? | Rejected | The EPA Healthy Homes Guide does not provide guidance on this topic and therefore will not be included in the SWS.
Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Scheduling | April 21, 2014 | April 21, 2014 | 2.0403.2a | This is impractical. The vapor retarder/barrier helps keep workers off the materials that are left behind. Higher puncture resistance products would work better and allow for fewer repairs at the end. | Accepted with Modifications | The detail was editted to be outcome based rather than processed base; therefore, the title of "Scheduling" was changed to "Material integrity". | Change Spec to: Title: Material Integrity Specification: Care will be taken to prevent punctures during installation Ojective: Protect ground moisture barrier from damage during other crawl space work
Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Coverage | April 21, 2014 | April 21, 2014 | 2.0403.2b | The barrier should be installed in accordance with the manufacture's instructions and ASTM E1643. Penetrating fasteners are not recommended. Ballast is generally not necessary. | Accepted |  | An air barrier and ground moisture barrier, covering 100% of the exposed crawl space floor, will be installed and sealed to the wall's air and moisture barrier in accordance with ASTM E1643 and manufacturer's recommendations Ground moisture barrier will be fastened to ground in accordance with manufacturer's recommendations with durable fasteners or ballast(s) and extend a minimum of 6" up the foundation wall
Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Material specification | April 21, 2014 | April 21, 2014 | 2.0403.2c | ASTM D703 has been withdrawn. It was replaced with D4549. However, the industry accepted test method for vapor retarders is ASTM E1745. Class A offers the best puncture resistance (2200g and Class B at 1700g) as tested in accordance with ASTM D1709. | Accepted |  | A ground moisture barrier with a rating of no more than 0.1 perm will be used A minimum expected service life of 10 years will be ensured A ground moisture barrier will be used that meets tear and puncture resistance standard ASTM D703 ASTM D1745
Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Fastening | April 21, 2014 | April 21, 2014 | 2.0403.2e | Penetrating fasteners are not recommended. Installation in accordance with manufacturer's instructions and ASTM E1643 would be more appropriate. | Accepted with Modifications |  | The air barrier and ground moisture barrier will be fastened to the ground to prevent movement in accordance with ASTM E1643 and manufacturer's recommendations A minimum expected service life of 10 years will be ensured
Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Vapor Retarders on Walls | Air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 | April 21, 2014 | April 21, 2014 | 2.0403.3a | "2012 IRC R408.3 does not require a vapor retarder on crawl space walls. Polyethlene sheeting will trap moisture and can contribute to mold growth. This method should not be used over fiberglass batts. The wall needs to be allowed to breath with vapor permeable products or encased in spray foam to avoid a dew point forming in the assembly." | Rejected | The 2012 IRC R408.3 requires vapor barrier 6" above grade.
Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Vapor Retarders on Walls | Coverage | April 17, 2014 | April 17, 2014 | 2.0403.3b | I really don't like the idea of installing vapor barriers on the interior of foundation walls. It is wishful thinking that the vapor barrier will mitigate moisture problems if the exterior wall isn't waterproofed or dampproofed. I think that the 6-inch ground moisture barrier overlap onto the wall is good practice but that running the vapor barrier further up the wall is pointless and could be counterproductive. | Further Investigation Required | The committee is reviewing literature before defining a path forward.
Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Vapor Retarders on Walls | Coverage | March 31, 2014 | March 31, 2014 | 2.0403.3b | This spec varies from the IRC, which says take the vapor barrier 6 inches up the wall. I think it is bad practice to install a vapor barrier on the inside of a crawl space wall, higher than 6 inches. The vapor barrier reduces drying potential and could harbor pests. What about the ventilation that the IRC requires? I don't think that is always necessary, but the IRC says you need 1/1500 of natural or an exhaust fan connect to the living space or a supply register in the crawl space of a home that doesn't have AC. The "doesn't have AC" is my spec responding to an oversight in the code and in common building practice. | Further Investigation Required | The committee is reviewing literature before defining a path forward.
Manufactured Housing | Health and Safety | Moisture | Vapor Barriers | Pier and Skirting Foundations&mdash;Ground Moisture Barriers | Fastening | April 18, 2014 | April 18, 2014 | 2.0403.4d | The minimum expect service life of ten years is one of those statements that seems like obligatory blather. Either use a good spec or none at all. Enough of these vague statements and the credibility of the standard becomes a question. | Accepted |  | Ground moisture barrier may be fastened to ground with durable fasteners Delete this text: A minimum expected service life of 10 years will be ensured
Manufactured Housing | Health and Safety | Moisture | Vapor Barriers | Pier and Skirting Foundations&mdash;Ground Moisture Barriers | Fastening | March 31, 2014 | March 31, 2014 | 2.0403.4d | I like this spec whenever the GMB is sealed, which it should be in most all installations. In porous soils, the GMB will flap around in the wind and make noise of it's sealed. High wind could displace the GMB if it isn't sealed. Durable fasteners such as geotextile staples? | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Health and Safety | Moisture | Space Conditioning | Closed Crawl Spaces&mdash;Crawl Space Conditioning | No return pathway to living space | April 17, 2014 | April 17, 2014 | 2.0404.3a | Even though allowed by code, this is a bad idea. In many regions, 50% of homes are air conditioned. Do you like the idea of air conditioning a crawl space? By the way the IRC requires a "return air pathway to a common area" when conditioning a crawl space. I suggest striking this option. | Accepted with Modifications | Maintain consistency with 2012 IRC
Single-Family Homes | Health and Safety | Moisture | Space Conditioning | Closed Crawl Spaces&mdash;Crawl Space Conditioning | No return pathway to living space | April 21, 2014 | April 21, 2014 | 2.0404.3a | If the crawl space is within the thermal and pressure boundaries of the building, sealing all penetrations should not be mandatory. Not all crawl spaces have IAQ problems. | Rejected | The section is about return air pathways, not penetrations.
Single-Family Homes | Health and Safety | Moisture | Space Conditioning | Closed Crawl Spaces&mdash;Crawl Space Conditioning | Option 2: supply air | April 18, 2014 | April 18, 2014 | 2.0404.3c | By pressurizing the crawl space are we driving crawl space air into the living space? We air condition the crawl space in the summer. This is a bad option. Suggest striking this option. | Rejected | Maintain consistency with 2012 IRC. Additionally, there are other options provided in the SWS to perform this detail.
Single-Family Homes | Health and Safety | Moisture | Space Conditioning | Closed Crawl Spaces&mdash;Crawl Space Conditioning | Option 2: supply air | March 31, 2014 | March 31, 2014 | 2.0404.3c | Never seen a backdraft damper on a branch duct or register. This spec should be limited to heating-only systems. Otherwise the AC will refrigerate the crawl space and make moisture problems worse. | Rejected | A back flow damper is recommended to keep crawlspace air from entering living space. The committee is unaware of research that supports the comment. Additionally, other options are provided in the SWS to perform this detail.
Single-Family Homes | Health and Safety | Moisture | Space Conditioning | Closed Crawl Spaces&mdash;Crawl Space Conditioning | Option 3: conditioned house air | April 21, 2014 | April 21, 2014 | 2.0404.3d | I don't understand the difference between 3d and 3e. Neither is a code-approved approach is it? Why are these two sections covered in "space conditioning"? Neither option conditions the crawl space. I suggest another detail called "power-ventilated crawl space" or something like that. | Rejected | Option 3 and Option 4 are different. Option 4 is an explicit option per IRC: R408.3:2.1. Additionally, there are other options provided in the SWS to perform this detail.
Single-Family Homes | Health and Safety | Moisture | Space Conditioning | Closed Crawl Spaces&mdash;Crawl Space Conditioning | Option 4: exhaust | March 31, 2014 | March 31, 2014 | 2.0404.3e | According to IRC 2012, the make-up air for this fan comes from "an air pathway to a common area (such as a duct or transfer grille) IRC R408.3: 2.2. Some retrofitters use the crawl space fan as a whole-building ventilation fan and claim it works very well for both functions. | Accepted with Modifications | The language was modified to maintain consistency with 2012 IRC. This use of a crawlspace fan for whole building ventilation is in violation of ASHRAE 62.2. | Specification 2.0404.3a was removed and the lanaguage was added to Option 1 and Option 3.
Single-Family Homes | Health and Safety | Moisture | Space Conditioning | Closed Crawl Spaces&mdash;Crawl Space Conditioning | Monitoring alarm system | April 17, 2014 | April 17, 2014 | 2.0404.3f | Do you really believe that anyone will use this standard? | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Health and Safety | Moisture | Space Conditioning | Basements&mdash;Dehumidification | Dehumidification for divided spaces | April 21, 2014 | April 21, 2014 | 2.0404.4b | This is not necessary if the space is conditioned. We don't dry all basements. | Rejected | The detail identifies what to do if dehumidification is added.
Single-Family Homes | Health and Safety | Moisture | Space Conditioning | Basements&mdash;Dehumidification | Relative humidity | April 21, 2014 | April 21, 2014 | 2.0404.4c | How can that be ensured at a reasonable cost? | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Health and Safety | Moisture | Space Conditioning | Basements&mdash;Dehumidification | Condensing surfaces(e.g., cold water pipes) | April 21, 2014 | April 21, 2014 | 2.0404.4d | This is not necessary if the space is conditioned. | Rejected | The detail identifies what to do if dehumidification is added.
Single-Family Homes | Health and Safety | Moisture | Space Conditioning | Basements&mdash;Dehumidification | Dehumidification (option for dry climates and heating- dominated climates seasonally) | April 21, 2014 | April 21, 2014 | 2.0404.4e | How can that be ensured at a reasonable cost? | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Health and Safety | Radon | Air Sealing | Radon&mdash;Air Sealing Considerations | Radon testing and mitigation | April 21, 2014 | April 21, 2014 | 2.0501.1a | Will testing be an allowable expense? With limited funds, how will testing costs be covered, much less mitigation? | Rejected | This is a program issue, not an SWS issue.
Single-Family Homes | Health and Safety | Radon | Air Sealing | Radon&mdash;Basements and Crawl spaces | Radon testing and mitigation | April 21, 2014 | April 21, 2014 | 2.0501.2a | Will testing be an allowable expense? With limited funds, how will testing costs be covered, much less mitigation? | Rejected | This is a program issue, not an SWS issue.
Single-Family Homes | Health and Safety | Electrical | Knob and Tube Wiring | Knob and Tube Wiring | Knob and tube identification | March 13, 2014 | March 13, 2014 | 2.0601.1a | this is a test | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Health and Safety | Occupant Education and Access | Basements and Crawl Spaces | Crawl Spaces&mdash;Providing Access | Access | April 21, 2014 | April 21, 2014 | 2.0701.1a | This can't always be done in older homes. New construction codes cannot always be implemented in existing housing. | Rejected | If you are providing access, then the detail should be followed.
Single-Family Homes | Health and Safety | Occupant Education and Access | Basements and Crawl Spaces | Crawl Spaces&mdash;Providing Access | Access | April 17, 2014 | April 17, 2014 | 2.0701.1a | Why don't you give the dimensions for the hatch or door. 16 x 24 if vertical and outdoor 24 x 18 if through the floor indoor. | Rejected | If you are providing access, then the detail should be followed.
Single-Family Homes | Health and Safety | Occupant Education and Access | Basements and Crawl Spaces | Crawl Spaces&mdash;Providing Access | Lock | April 21, 2014 | April 21, 2014 | 2.0701.1b | This does not save energy or protect health and safety. It should not be a required part of weatherization. | Rejected | If you are providing access, then the detail should be followed.
Single-Family Homes | Health and Safety | Occupant Education and Access | Basements and Crawl Spaces | Crawl Space Information Sign | Hazard warning | April 17, 2014 | April 17, 2014 | 2.0701.2c | If the insulation installation assumed that the crawl space wouldn't be used for storage, the sign should say "don't store stuff down here". | Rejected | Committee does not agree with recommended lanuage.
Single-Family Homes | Health and Safety | Occupant Education and Access | Installed Equipment | Warranty and Service Agreement | Warranty renewal and service agreement | April 21, 2014 | April 21, 2014 | 2.0702.1b | Why would the program take on this additional burden and responsibility? | Rejected | A warranty only needs to be offered.
Single-Family Homes | Health and Safety | Occupant Education and Access | Installed Equipment | Warranty and Service Agreement | Warranty renewal and service agreement | March 3, 2014 | March 3, 2014 | 2.0702.1b | Could you clarify for me. I cant imagine low income occupants opting to buy a potentially expensive 10 year inspection and repair service warranty. Remove. | Rejected | A warranty only needs to be offered
Multifamily Homes | Health and Safety | Occupant Education and Access | Installed Equipment | Occupant and Building Staff Education&mdash;Low Rise | Carbon monoxide ( CO CO Carbon monoxide ) | April 11, 2014 | April 11, 2014 | 2.0702.2h | I don't see any need to install a CO alarm in apartments without any combustion appliances. I would amend the language to say: " A CO alarm will be installed in any dwellings containing combustion appliances." | Rejected | The citation of ASHRAE 62.2 states that CO detectors should be in all homes. ASHRAE 62.2 references NFPA 720 for the location of the CO detector.
Single-Family Homes | Air Sealing | Attics | Penetrations and Chases | Chase Capping | Joint seal | April 7, 2014 | April 7, 2014 | 3.1001.2e | Does DOE intend to provide a definition of durable through the SWS or other guidance? | Rejected | A definition is not going to be provided.
Single-Family Homes | Air Sealing | Attics | Open Stairwells | Interior with Sloped Ceiling | Pre-inspection | April 5, 2014 | April 5, 2014 | 3.1002.1a | I find the whole topic of open stairways very difficult to understand and illustrate. The whole discussion is relevant to open stairways to unconditioned basements as well. It might make more sense to talk about the stairway between a conditioned area and an unconditioned one and the choice of whether to include the stairway within the thermal boundary or to isolate the stairway with insulation and air sealing. Even if the stairway remains within the thermal boundary, we still should evaluate its walls as conduits for air leakage. | Rejected | This topic is addressed in 3.1002.3.
Single-Family Homes | Air Sealing | Attics | Open Stairwells | Interior with Sloped Ceiling | Perimeter sealing | April 21, 2014 | April 21, 2014 | 3.1002.1f | 3.1002.1f 3.1002.3e I want to be sure the language covers times when these assemblies adjoin exterior walls—in subsequent sections language clearly states to cover, seal, or foam stud bays that are exterior walls. This section should too. | Rejected | The current standard covers this situation.
Single-Family Homes | Air Sealing | Attics | Dropped Ceilings and Soffits | 3-D Walls | Pre-inspection | April 4, 2014 | April 4, 2014 | 3.1003.4a | I have no idea what you mean by 3-D Walls. | Accepted |  | Rename Detail title to "Dropped Ceilings"
Single-Family Homes | Air Sealing | Attics | Dropped Ceilings and Soffits | Dropped Ceiling with Light Boxes and Fixtures | Non-insulation contact ( IC IC Insulation contact ) rated recessed lights | April 21, 2014 | April 21, 2014 | 3.1003.5c | Please clarify: 1/2" from combustible materials - what is this referring to? Proper boxing, with 3" clearance can be safely installed over the fixture. | Accepted | The committee assumed that the 1/2" includes the box. | Remove "and at least ½" from combustible materials"
Single-Family Homes | Air Sealing | Attics | Other Ceiling Materials | Tongue and Groove Ceilings | Backing | April 21, 2014 | April 21, 2014 | 3.1005.1b | Please clarify how backing would be installed in a finished attic condition? | Rejected | Attic is defined as unfinished.
Single-Family Homes | Air Sealing | Attics | Other Ceiling Materials | Tongue and Groove Ceilings | Sealant selection | April 21, 2014 | April 21, 2014 | 3.1005.1c | Remove the "visible" portion of this specification. In many cases, this is the only practical solution. | Rejected | The language is necessary to ensure ceiling remains aesthetically pleasing.
Single-Family Homes | Air Sealing | Windows and Doors | Repairing/Replacing Cracked and Broken Glass | Fixed Frame with Wood Sash&mdash;Older House | New glass installation | April 21, 2014 | April 21, 2014 | 3.1202.1d | Clarify: Every time we remove glass we have to prime the sash? Some commercially available sealants do not require priming. | Accepted |  | Glass will be sized 1/8" to 3/16'' smaller than opening to allow for movement of frame Safety glass will be installed in accordance with local codes Push points will be provided on each side to secure glass in frame Glazing compound will be added in accordance with manufacturer specifications
Single-Family Homes | Air Sealing | Windows and Doors | Replacement | Fixed Frame with Wood Sash&mdash;Older House | Lead paint assessment | April 21, 2014 | April 21, 2014 | 3.1203.1a | Change heading to "Replacement Window in Existing Window Frame". In general the titles throughout the SWS could use some work to make them more specific. | Accepted |  | Detail Title: Replacement Window in Existing Window Frame
Single-Family Homes | Air Sealing | Basements and Crawl Spaces | Crawl Spaces | Closed Crawl Spaces&mdash;Air Sealing Exterior Wall | Pest exclusion | April 21, 2014 | April 21, 2014 | 3.1402.3b | Please clarify:What is the test for pest proof? Mice, termites and spiders are all pests, but require different materials. Does this mean we need to plug holes with steel wool? | Accepted | Pests are dependent on geographic location and location in house. | If penetration is greater than ¼", caulking, steel wool, or other pest-proof material will be used to fill the penetration before sealing
Single-Family Homes | Air Sealing | Basements and Crawl Spaces | Crawl Spaces | Closed Crawl Spaces&mdash;Attached Crawl Spaces Under Unconditioned Spaces | Entry point | April 21, 2014 | April 21, 2014 | 3.1402.5b | Most floors are framed 16” OC. This requirement means adding structural repairs to the cost. These are not easily accomplished and decrease SIR. Allow skinny people to use smaller opening. Consider that the space was not accessible previously, so making a standard-sized opening doesn't seem neccessary | Accepted |  | Access will be provided to all crawl spaces Access openings through the floor will be a minimum of 18" by 24" or as constrained by existing framing members Openings through a perimeter wall will be not less than 16" by 24" or as constrained by existing framing members When any portion of the through-wall access is below grade, an area way not less than 16" by 24" will be provided Under-floor spaces containing appliances will be provided with an unobstructed access large enough to remove the largest appliance but not less than 30" high and 22" wide or more than 20' long measured along the center line of the passageway from the opening to the appliance A level service space at least 30" deep and 30" wide will be present at the front or service side of the appliance If the depth of the passageway or the service space exceeds 12" below the adjoining grade, the walls of the passageway will be lined with concrete or masonry extending 4" above the adjoining grade in accordance with Chapter 4 2012 IRC The rough-framed access opening dimensions will be a minimum of 22" by 30" and large enough to remove the largest appliance
Single-Family Homes | Air Sealing | Basements and Crawl Spaces | Crawl Spaces | Closed Crawl Spaces&mdash;Attached Crawl Spaces Under Unconditioned Spaces | Entry point | April 21, 2014 | April 21, 2014 | 3.1402.5b | Delete "Access will be provided to all crawlspaces" | Accepted |  | When adding access to a crawl space: Access will be provided to all crawl spaces Access openings through the floor will be a minimum of 18" by 24" or as constrained by existing framing members Openings through a perimeter wall will be not less than 16" by 24" or as constrained by existing framing members When any portion of the through-wall access is below grade, an area way not less than 16" by 24" will be provided Under-floor spaces containing appliances will be provided with an unobstructed access large enough to remove the largest appliance but not less than 30" high and 22" wide or more than 20' long measured along the center line of the passageway from the opening to the appliance A level service space at least 30" deep and 30" wide will be present at the front or service side of the appliance If the depth of the passageway or the service space exceeds 12" below the adjoining grade, the walls of the passageway will be lined with concrete or masonry extending 4" above the adjoining grade in accordance with Chapter 4 2012 IRC The rough-framed access opening dimensions will be a minimum of 22" by 30" and large enough to remove the largest appliance
Single-Family Homes | Air Sealing | Basements and Crawl Spaces | Special Considerations | Skirting Post and Pier Foundations | Skirting | April 21, 2014 | April 21, 2014 | 3.1488.1a | Remove this specification | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Air Sealing | Ducts | Duct Preparation | Preparation and Mechanical Fastening | Metal to metal | April 21, 2014 | April 21, 2014 | 3.1601.1b | Delete "with a minimum of 3 equally spaced screws" | Accepted |  | Round ducts will be mechanically fastened to maintain alignment Other shaped ducts will be securely fastened and sealed with welds, gaskets, mastics (adhesives), mastic-plus-embedded-fabric systems, or tapes
Single-Family Homes | Air Sealing | Ducts | Duct Sealing | Air Sealing Duct System | New component to existing component | April 21, 2014 | April 21, 2014 | 3.1602.1b | Please clarify: does this mean all duct leaks need to be sealed? We believe that duct sealing at this level is only effective when the duct is outside of the conditioned space, or when there are IAQ problems in the basement/crawl space. | Rejected | This specification only applies to new to existing components when called for.
Single-Family Homes | Air Sealing | Ducts | Duct Sealing | Air Sealing System Components | Duct boot to interior surface | April 21, 2014 | April 21, 2014 | 3.1602.4a | Differentiate between ducts in conditioned and unconditioned spaces | Accepted |  | All gaps between boot and interior surface that defines conditioned space will be air sealed Gypsum edge will be wetted before applying water-based sealant Sealants will be continuous and be in accordance with 2012 IRC R302.9
Single-Family Homes | Air Sealing | Ducts | Duct Sealing | Capping Dual-Cooling Up-Ducts | Backing and infill | April 1, 2014 | April 1, 2014 | 3.1602.6a | Consider eliminating this standard. Very few readers will understand this. I'm not sure what you mean. If the evap cooler is still used and the upducts function for relief, you may be disabling the cooler by sealing the up-ducts. Are we taking the up-ducts permanently out of service or is this a seasonal solution? Very vague standard. | Rejected | This specification is not prescriptive. If the auditor determines this specification is the appropriate measure for a given house, this is the specification outlining desired outcomes.
Single-Family Homes | Air Sealing | Ducts | Duct Sealing | Return and Supply Plenums in Basements and Crawl Spaces | Supply plenums (includes conditioned crawl spaces) | April 21, 2014 | April 21, 2014 | 3.1602.7a | The desired outcome above lists crawl spaces but in the detail it includes basements. What about conditioned basements that are a living space? | Accepted |  | Change desired outcome of the detail to: Connections between the crawl space/unconditioned basement and living space eliminated to improve indoor air quality ( IAQ ) and efficiency of the distribution system In objectives for 3.1602.7 a and b: Eliminate connection between the crawl space/unconditioned basement and living space
Single-Family Homes | Air Sealing | Ducts | Duct Sealing | Return and Supply Plenums in Basements and Crawl Spaces | Supply plenums (includes conditioned crawl spaces) | April 1, 2014 | April 1, 2014 | 3.1602.7a | Not enough information. Is this condition a walk-away. Do we expect weatherization to install a new duct system. This reads like a standard for a new building. | Rejected | This specification is not prescriptive. If the auditor determines this specification is the appropriate measure for a given house, this is the specification outlining desired outcomes.
Single-Family Homes | Insulation | Non-Insulation Contact (IC) Recessed Light |  |  |  | 2013-04-20 | 2014-04-20 | 4.1001.1 | Provide that Wx crew may install an industry air tight can insert that includes a temperature switch as an alternative. Reference: Home Energy Magazine, article on measured temperatures of recessed fixtures comparing various air sealing practices. Provide that, with resident/owner OK, the fixture(s) may be replaced with a surface mounted fixture and opening sealed. | Accepted with Modifications | The specification will be modified to give discretion to the authority having jurisdiction to allow other air sealing measures | A fire-rated air barrier system (i.e., equivalent to 5/8 fire code gypsum wallboard) will be used to separate non- IC rated recessed lights from insulation, using one of the methods below: A fire-rated airtight closure taller than surrounding attic insulation will be placed over non- IC rated recessed lights OR The non- IC rated light fixture will be replaced with an airtight and IC - rated fixture OR The fixture(s) may be replaced with surface mounted fixture and opening sealed. OR Air sealing measures as approved by the authority having jurisdiction.
Single-Family Homes | Insulation | Attics | General Preparation | Non-Insulation Contact (IC) Recessed Light | Air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary system | April 1, 2014 | April 1, 2014 | 4.1001.1a | I could not find an air-sealing SWS for non-IC rated recessed lights. Instead, the air sealing instructions are nested (hidden) in the preparation for attic insulation. I suggest adding an entry for air sealing as a stand alone. | Accepted |  | Recommend copying this and adding as a new detail that is "air sealing for non-IC rated recessed lights" in 3.1001.X Language should mirror recommended edit for 4.001.1: A fire-rated air barrier system (i.e., equivalent to 5/8 fire code gypsum wallboard) will be used to separate non- IC rated recessed lights from insulation, using one of the methods below: A fire-rated airtight closure taller than surrounding attic insulation will be placed over non- IC rated recessed lights OR The non- IC rated light fixture will be replaced with an airtight and IC - rated fixture OR The fixture(s) may be replaced with surface mounted fixture and opening sealed.
Single-Family Homes | Insulation | Attics | General Preparation | Non-Insulation Contact (IC) Recessed Light | Enclosure top | April 21, 2014 | April 21, 2014 | 4.1001.1b | Change to allow for fire-retardant insulation over top of air sealed enclosure | Rejected | Fire-retardant insulation over top of air sealed enclosure is not allowable by current code, IRC E4004.9.
Single-Family Homes | Insulation | Fireplace Chimney and Combustion Flue Vents |  |  |  | 2013-04-20 | 2014-04-20 | 4.1001.3 | Provide that vent, chimney, or other heat generating device surface may be coated with intumescent paint, and rock wool or other non-combustible insulation placed in contact with the device. | Rejected | This comment is addressed in specification 4.1001.3c, where insulation material must be rated for contact with heat generating sources.
Single-Family Homes | Insulation | Attics | General Preparation | Dense Pack Preparation | Preparation | April 21, 2014 | April 21, 2014 | 4.1001.5a | ADD: Shrouds and containment devices are highly recommended. | Accepted |  | Lead safety procedures will be followed Cavities will be free of hazards, intact, and able to support dense pack pressures All escape openings will be blocked for material Access will be gained and each cavity will be probed, locating all attic floor joists and blockers Interior will be masked and dust controlled during drilling when accessing from interior, shrouds and containment devices are recommended Electricity supply will be confirmed and will support blowing machine power demand Blowing machine pressure test will be performed with air on full, feed off, agitator running, and gate closed Hose outlet pressure will be at least 80" of water column ( IWC ) or 2.9 pounds per square inch ( psi ) for cellulose insulation; for other types of dense pack insulation, check manufacturer specifications for blowing machine set up
Single-Family Homes | Insulation | Attics | General Preparation | Dense Pack Preparation | Preparation | April 21, 2014 | April 21, 2014 | 4.1001.5a | Dense-pack can be achieved at even lower PSI ratings but at a severe cost to production. If we want agencies/companies to obtain better SIR’s and actually achieve Dense-pack results, we may want to bump this up to 3.5 or even 4.0. Understood that 2.9 is bottom-line, but building a cushion may be beneficial. | Rejected | The specification states the minimum PSI rating. See manufacturers' recommendations for detailed information.
Single-Family Homes | Insulation | Unvented Roof Deck—Preparation for Spray Polyurethane Foam |  |  |  | 2013-04-20 | 2014-04-20 | 4.1001.6 | Remove insulation at owners option, especially if space is separatel heated/cooled, more especially if zoning is an option or desired, and to serve owners preferences how they wish to reside in their house, e.g., sound insulation may be desired. | Further Investigation Required | Committee to reach out to industry representatives to see if there is testing or code that relate to this comment.
Single-Family Homes | Insulation | Attics | Above Roof Deck Insulation | Preparation | Roof covering removal | March 27, 2014 | March 27, 2014 | 4.1002.1a | Main heading is too general. Should be Above Roof Deck Insulation: Preparation | Accepted |  | Change detail title to: Above Roof Deck Insulation: Preparation
Single-Family Homes | Insulation | Attics | Above Roof Deck Insulation | Preparation | Roof covering replacement | March 19, 2014 | March 19, 2014 | 4.1002.1b | This should also be included in the mobile home specifactions. In Oregon, we routinely install exterior roof insulation in conjuction with an exterior roof membrane (EPDM, TPO, PVC)I have also suggested adding this to 4.1003.9e - Patching and sealing openings, but maybe the exterior membrane could simply be included under under this spec. It would simply have to be added to the mobile home specs. | Accepted |  | Recommend adding this to the MH SWS.
Single-Family Homes | Insulation | Attics | Above Roof Deck Insulation | Installation | Sealing | March 27, 2014 | March 27, 2014 | 4.1002.2a | Top heading too general. Include Above Deck Roof Deck Insulation | Accepted |  | Above Deck Roof Deck Insulation: Installation
Single-Family Homes | Insulation | Attics | Above Roof Deck Insulation | Installation | Sealing | March 19, 2014 | March 19, 2014 | 4.1002.2a | This should also be included in the mobile home specifactions. In Oregon, we routinely install exterior roof insulation in conjuction with an exterior roof membrane (EPDM, TPO, PVC) | Accepted |  | Recommend adding this to the MH SWS.
Single-Family Homes | Insulation | Attics | Above Roof Deck Insulation | Installation | Installation | March 19, 2014 | March 19, 2014 | 4.1002.2b | This should also be included in the mobile home specifactions. In Oregon, we routinely install exterior roof insulation in conjuction with an exterior roof membrane (EPDM, TPO, PVC) | Accepted |  | Recommend adding this to the MH SWS.
Single-Family Homes | Insulation | Attics | Above Roof Deck Insulation | Installation | Occupant education | March 19, 2014 | March 19, 2014 | 4.1002.2c | This should also be included in the mobile home specifactions. In Oregon, we routinely install exterior roof insulation in conjuction with an exterior roof membrane (EPDM, TPO, PVC) | Accepted |  | Recommend adding this to the MH SWS.
Single-Family Homes | Insulation | Pitched/Vaulted/Cathedralized Ceilings—Dense Pack Over |  |  |  | 2013-04-20 | 2014-04-20 | 4.1003.2 | Provide alternate to allow loose fill blown insulation. Impose fan-forced positive pressure from outdoors into each isolated framed cavity, to space above insulation, for three coldest months in cold climates (adjust duration for other climates). Note that this method, I'm told proposed by J. Lstiburek decades ago, has not been field verified. Align 4.1003.2 with BSci "Dense Pack Roof Assemblies" | Further Investigation Required | We cannot support field testing via the Standard Work Specifications, however, options are being investigated for addressing this.
Single-Family Homes | Insulation | Attics | Attic Ceilings | Pitched/Vaulted/Cathedralized Ceilings&mdash;Dense Pack Over | Fill slant ceilings | March 27, 2014 | March 27, 2014 | 4.1003.2a | I think the density of insulation is too high becasue of the size of the cavity. I would specify fiberglass or rock wool only, no cellulose. | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Insulation | Attics | Attic Ceilings | Cape Cod Side Attic Roof&mdash;Dense Pack Installation | Netting, fabric, rigid sheathing | April 21, 2014 | April 21, 2014 | 4.1003.4b | Don't prescribe how far apart staples should be; install according to manufacturer's specs and fastener load capabilities. | Accepted |  | When using netting or fabric, staples will be placed every 1 ½" on center, or in accordance with manufacturer specifications Netting or fabric will meet local fire codes Rigid materials will close the cavity
Manufactured Housing | Insulation | Attics | Attic Ceilings | Installing Fiberglass Blown Insulation for Flat, Bowed, or Vaulted Ceilings (via Exterior Access from Top of Roof) | Patching and sealing openings | March 19, 2014 | March 19, 2014 | 4.1003.9e | After reviewing my previous submittal. Perhaps somehting as simple as this would be more appropriate.: The roof membrane must cover the entire roof and the New roof covering will be installed in accordance with manufacturer specifications and local building code requirements. | Rejected | If the program allows a new roof for a manufactured house, then a new roof should be installed.
Manufactured Housing | Insulation | Attics | Attic Ceilings | Installing Fiberglass Blown Insulation for Flat, Bowed, or Vaulted Ceilings (via Exterior Access from Top of Roof) | Patching and sealing openings | March 19, 2014 | March 19, 2014 | 4.1003.9e | There appears to be an omission on patching of holes in this section. In the Northwest, we get considerable rain. We rarely simply patch penetrations of the mobile home roof as experience has shown that most will eventually leak due to constant rainfall. We most times install either a TPO, PVC or EPDM roof membrane over the blown ceiling cavity and a layer of rigid insulation on the exterior of the roof. This is not a listed option. I intend to use the field guide utility on this website, but if there is no spec to list,I am unsure if I can come up with the specific details needed to create what I need. I would recommend adding language such as follows: If exterior roof membrane is used: A durable exterior roof membrane will be installed according to manufacturers instructions. The roof membrane must cover the entire roof and be extended down the wall and over the top edge of the wall covering and secured along the entire perimeter using non-corrosive, self-tapping hex-head with a minimum length of 1 ¼ inch metal screws with butyl tape installed between a termination bar and the roof covering. All plumbing vents, kitchen fans, bath fans, wood stoves, and other fixtures must be vented to the outside of the new roof and be adequately flashed and sealed. Roof insulation and covering shall be sufficiently rigid to prevent “ponding” of water on the surfaces after installation. All pre-existing roof drainage systems shall function properly after the insulation and the new roof covering have been installed. | Rejected | Commenter rejected this comment in favor of a revised comment for 4.1003.9e, which was rejected as well.
Single-Family Homes | Insulation | Attics | Knee Walls | Preparation for Dense Packing | Backing | April 21, 2014 | April 21, 2014 | 4.1004.1a | Don't specify staple size and spacing. | Accepted |  | All knee walls will have top and bottom plate or blockers installed using rigid materials When knee wall floor and walls are being insulated, the floor joist running under the knee wall will be air sealed If fabric is used before dense packing, it will be secured with 1" crown staples every 2" according to manufacturers specifications or with furring strips every wall stud If rigid material is used, material will be installed to cover 100% of the surface of the accessible knee wall area If foam sheathing is used, sheathing will be listed for uncovered use in an attic or covered with a fire barrier
Single-Family Homes | Insulation | Attics | Knee Walls | Strapping for Existing Insulation | Attachment | April 17, 2014 | April 17, 2014 | 4.1004.3c | Strapping material is not defined or properties explained. Explain covering entire insulation or just minimum ability to hold insulation in place. Strapping must be better defined. | Rejected | The objective to maintain alignment speaks to the nature of this comment.
Single-Family Homes | Insulation | Attics | Attic Floors | Accessible Floors&mdash;Loose Fill Installation | Preparation | April 21, 2014 | April 21, 2014 | 4.1005.2a | If no additional insulation is added to floored cavity: strike need to mark depth of insulation. You must assume the cavity is going to be completely filled, and markers on a bare wood floor won't withstand any traffic or storage boxes covering them. | Rejected | Comment is based on improper assumptions.
Single-Family Homes | Insulation | Attics | Attic Floors | Accessible Floors&mdash;Loose Fill Installation | Onsite documentation | April 1, 2014 | April 1, 2014 | 4.1005.2d | Insulation Documentation is inconsistent in this section. This spec is the most detailed (which I prefer). However, most specs have somethign to the effect of,"(4.1004.4d) Occupant education-Documentation of material and R-value will be provided to occupant-Provide occupant with documentation of installation." | Accepted with Modifications | Language was used from 16 CFR 460.17 and was also applied to other sections. | See attachment.
Single-Family Homes | Insulation | Attics | Attic Floors | Enclosed Bonus Room Floor Over Unconditioned Space&mdash;Dense Pack Installation | Fill floors | April 21, 2014 | April 21, 2014 | 4.1005.5b | This is the first place I saw an R value for fiberglass stated below 2.2- I know each manufacturer has different density for their formulation- maybe just leave it at “as PMI for air-sealing w/ fiberglass” In many categories the default is “Dense-Pack” and rightly so, but there are many situations where the pressure plane is completely tight- monolithic sheetrock walls for one. In those cases why require cavities to be blown to DP standards knowing a reduction in R value with cellulose, extra time and materials, etc? | Accepted |  | Each cavity will be 100% filled to consistent density: Cellulose material will be installed to a minimum density of 3.5 pounds per cubic foot Loose fiberglass material will be installed and will be specifically approved for air flow resistance to a minimum density of 1.5 to 2 pounds per cubic foot per the manufacturer's recommendations The number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference
Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | April 21, 2014 | April 21, 2014 | 4.1006.1a | Equal R value to rest of attic is a big burden when it is small fraction of area. The extra weight causes severe problems in lifting the cover. Add language to require a counter-weight system and less R-value. R25 is sufficient in most cases, or set a range: small pop-up hatches full R value. Higed-style, R 25. But the counter-weight is critical since you require rigid foam and it can get heavy for elderly to open if no counter-weight is supplied. | Accepted |  | Hatches will be insulated to the maxium R-value structurally allowable up to the R-value of the adjoining insulated assembly with non-compressible insulation and the measure will include a protective barrier or baffle Pull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulation Counter-weights should be considered to ease accessiblity for excessively heavy hatches
Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | April 21, 2014 | April 21, 2014 | 4.1006.1a | Compressible insultation (such as fiberglass batts) should be allowed, especially for low pitched roofs. The limit on R value should be the same as the attic or as struturally allowable. | Accepted |  | Hatches will be insulated to the maxium R-value structurally allowable up to the R-value of the adjoining insulated assembly with non-compressible insulation and the measure will include a protective barrier or baffle Pull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulation Counter-weights should be considered to ease accessiblity for excessively heavy hatches
Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | March 28, 2014 | March 28, 2014 | 4.1006.1a | I think that having the same R-value as the assembly is unrealistic. I'd be real happy with 3 inches of PIC, which is around R-20. That would be difficult enough. How would you insulate this assembly to R-40? | Accepted |  | Hatches will be insulated to the maxium R-value structurally allowable up to the R-value of the adjoining insulated assembly with non-compressible insulation and the measure will include a protective barrier or baffle Pull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulation Counter-weights should be considered to ease accessiblity for excessively heavy hatches
Single-Family Homes | Insulation | Access Doors and Hatches |  |  |  | 2013-04-20 | 2014-04-20 | 4.1006.2 | To form a dam around hatch opening, place R30 wrapped fiberglass blanket, atop R19 insulation. Place R30 blanket atop hatch that has 4in of XPS adhered solidly (R49 hatch). Paint 5/8 inch gyp board hatch with semigloss latex and cover edges with J bead. Weatherstrip hatch with closed cell foam tape stapled at ends. Hatch treatment shall not make access more difficult or dangerous than with treatment described above. For reference see > http://www.southface.org/ez/media/homeenergyprojects.pdf | Rejected | This practice is not prohibited by the SWS.
Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Installation | April 21, 2014 | April 21, 2014 | 4.1006.2a | Compressible insultation (such as fiberglass batts) should be allowed, especially for low pitched roofs. The limit on R value should be the same as the attic or as struturally allowable. | Accepted |  | Hatches will be insulated to the maxium R-value structurally allowable up to the R-value of the adjoining insulated assembly with non-compressible insulation and the measure will include a protective barrier or baffle Attic hatches rough opening will be surrounded with a durable protective baffle that is higher than the level of the surrounding attic floor insulation
Single-Family Homes | Insulation | Attics | Special Considerations | Attic Ventilation | Air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow | March 4, 2014 | March 4, 2014 | 4.1088.1a | The first two bullets in this specification should be deleted, and the word "after" in the leading sentence replaced with "if". Research has shown that attic ventilation is not generally important in controlling moisture in attics or for shingle life. Moisture control is best done through the air sealing that is being verified or specified, and shingle life is much more dependent on shingle color. The original reason for attic ventilation was to control moisture, and technology in the 1930s did not lend itself well to comprehensive attic air sealing. Today's air sealing achieves the same end, in a more energy efficient manner. Bill Rose has also published articles based on his measurements in a test facility that show that ventilation had little importance on attic performance. Bill has also made a series of videos that are on YouTube as private videos, available from Bill upon request. The only marginally valid reason for systematic installation of attic venting is to comply with codes that require it in the local jurisdiction, until such time as codes catch up to the science and stop this requirement. | Accepted with Modifications | The specification was amended to keep the additional content if attic ventilation is required by local code. | Attic ventilation will be recommended or installed if local code requires attic ventilation during weatherization or retrofits The presence of an effective air barrier and thermal boundary between the attic and the living space must be verified and appropriate attic sealing and proper insulation is specified as part of the scope of work Local code requires attic ventilation during weatherization or retrofits
Single-Family Homes | Insulation | Walls | Preparation | Exterior Wall Dense Packing | Preparation | April 17, 2014 | April 17, 2014 | 4.1101.1a | Preparation notes "free of hazards", but does not specifically address knob and tube wiring. EX: "knob and tube wiring certified as safe for insulation fill." | Rejected | A specification in health and safety addresses knob and tube wiring.
Single-Family Homes | Insulation | Walls | Accessible Walls | Open Wall Insulation&mdash;General | Sealing | April 21, 2014 | April 21, 2014 | 4.1102.1a | Suggest calling the subtopic: Open-Cavity Walls | Accepted |  | Change subtopic and detail title to: Open-Cavity Walls. This will result in a change to 4.1102.1 and .2
Single-Family Homes | Insulation | Floors | Accessible Floors | Standard Floor System&mdash;Batt Installation | Installation | April 21, 2014 | April 21, 2014 | 4.1301.1b | Install fiberglass batts to R-32 value. 2x10 framing, 24" OC | Rejected | R-value requirements vary by climate and on-site situations.
Single-Family Homes | Insulation | Floors | Accessible Floors | Standard Floor System&mdash;Loose Fill with Netting | Netting, fabric | April 21, 2014 | April 21, 2014 | 4.1301.2b | Don't prescribe how far apart staples should be; install according to manufacturer's specs and fastener load capabilities. | Accepted |  | When using netting or fabric, staples will be placed according to manufacturer specifications every 1 ½" on center Netting or fabric will meet local fire codes
Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Closed Crawl Spaces&mdash;Wall Insulation | Insulation selection | March 31, 2014 | March 31, 2014 | 4.1402.1a | This spec is vague and misses the main issues of insulating crawl space walls. What do you mean by non-absorbent and fire rated? Does non-absorbent mean no fibrous insulation: That wouldn't be a bad decision. Fiberglass only absorbs 7% water by weight but the common facings used in crawl spaces are vapor barriers, which hinder drying. Fiberglass batts aren't a bad choice for dry climates: suggest < 20 inches of precip and <60% average rh. However, the vapor-barrier facing is still a problem. I think that by fire-rated you mean 25 or less flame spread or Class I or Class A rating. Might as well mention all of these ratings. | Further Investigation Required | This is a valid comment and the committee requests the commenter to submit required revisions to the text.
Single-Family Homes | Insulation | Ducts | Insulating Ducts | Insulating Flex Ducts | Removal of existing flexible ducting | April 21, 2014 | April 21, 2014 | 4.1601.1a | Clarify: remove uninsulated flex ducts in conditioned space? | Rejected | If the energy auditor determines that flex duct must be removed, then this specification provides the necessary detail.
Single-Family Homes | Insulation | Ducts | Insulating Ducts | Insulating Flex Ducts | Selection of new flexible ducting | April 21, 2014 | April 21, 2014 | 4.1601.1b | Clarify: New flex duct in conditioned space must be insulated? | Rejected | If the energy auditor determines that flex duct must be insulated, then this specification provides the necessary detail.
Single-Family Homes | Heating and Cooling | Forced Air | Design | Ductwork and Termination Design | Duct design | March 25, 2014 | March 25, 2014 | 5.3001.2a | Seal return duct from register under living room front window to the furnace | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Place appliance in operation | April 9, 2014 | April 9, 2014 | 5.3003.14a | Where is the complement to Combustion Analysis for gas-fired appliances for single family homes? | Accepted with Modifications | A similar content tab was added for signl-family housing. | Copy tab for SF housing.
Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Occupant Education | Routine maintenance | March 6, 2014 | March 6, 2014 | 5.3003.7f | WPN 13-5 identifies "Furnace or air conditioner filters" as eligible weatherization measures. Do Separate SWS exist for installing these measures? | Accepted with Modifications | The recommended addition mirrors direction from another section and it should be placed here for clarification. | Proper filter selection and how to change the filter will be explained to occupant. Importance of keeping outside unit clear of debris, vegetation, decks, and other blockage will be explained to occupant. Importance and timing of routine professional maintenance will be explained to occupant. There will be no air bypass around the filters and new central forced air HVAC systems will have minimum MERV 6 filtration.
Multifamily Homes | Heating and Cooling | Forced Air | Special Considerations | Regional Considerations&mdash;Low Rise | Very cold | April 10, 2014 | April 10, 2014 | 5.3088.2a | This comment is meant for the Detail level (as opposed to spec level). Rename the Detail "Regional Climatic Considerations...". "Regional Considerations" sounds like it could be any number of types of considerations, such as cultural, dialect, etc. | Accepted |  | Detail Title: Regional Climatic Considerations
Multifamily Homes | Heating and Cooling | Forced Air | Special Considerations | Regional Considerations&mdash;Mid and High Rise | Very cold | April 10, 2014 | April 10, 2014 | 5.3088.3a | This comment is meant for the Detail level (as opposed to spec level). Rename the Detail "Regional Climatic Considerations...". "Regional Considerations" sounds like it could be any number of types of considerations, such as cultural, dialect, etc. | Accepted |  | Detail Title: Regional Climatic Considerations
Single-Family Homes | Heating and Cooling | Hydronic Heating (Hot Water and Steam) | Equipment Maintenance, Testing, and Repair | Maintenance: Gas Boiler Service Inspection | Flue gas testing | April 1, 2013 | March 12, 2014 | 5.3104.2f | At 5.3104.2f Flue Gas Testing, references compliance with BPI-1100-T-2012, but the referenced Home Energy Audit Standard does not seem to have any description or limit for undiluted flue gas content (or whatever else was supposed to be at this reference). | Further Investigation Required | Currently there are discussions in the industry around CAZ testing. When the issue is resolved, the SWS will be updated.
Single-Family Homes | Heating and Cooling | Shading | Landscaping | Indigenous Shading | Plant selection | March 18, 2014 | March 18, 2014 | 5.3201.1a | test1234 | Rejected | Insufficient information provided by commenter. No actionable comments to respond to in the comment text.
Single-Family Homes | Ventilation | Exhaust | Components | Ducts | Duct design and configuration | April 1, 2013 | March 12, 2014 | 6.6002.1a | Section 6.60, on Exhaust Ventilation, never seems to require that ALL DUCTS terminate outside. The paragraphs specific to range hood and dryer (6.6005.1 & 6.6005.2) do so, but not the general 6.6002.1 Ducts, or 6.6002.2 Terminations (where one would expect it!). I was also very surprised at the requirement of R8 for ventilation (as compared to HVAC) duct insulation. [This actually pertains to the desired outcome for 6.6002.1 as a whole] | Accepted with Modifications | Change 6.6002.2f to include terminations to the outdoors to align with range hood and dryer (6.6005.1 & 6.6005.2) | Change 6.6002.2f: Terminations will be ducted to the outdoors, which does not include unconditioned spaces such as attics and crawl spaces that are ventilated with the outdoors. Terminations will be installed: A minimum of 3' away from any property line A minimum of 3' away from operable opening to houses A minimum of 10' away from mechanical intake As required by authority having jurisdiction
Single-Family Homes | Ventilation | Exhaust | Components | Ducts | Duct insulation | April 21, 2014 | April 21, 2014 | 6.6002.1b | Wisconsin believes R-6 is sufficient for exhaust ventilation. | Rejected | SWS as written already allows R-values to be in compliance with the local codes.
Single-Family Homes | Ventilation | Exhaust | Components | Terminations | Hole in building shell | April 1, 2013 | March 12, 2014 | 6.6002.2a | Section 6.60, on Exhaust Ventilation, never seems to require that ALL DUCTS terminate outside. The paragraphs specific to range hood and dryer (6.6005.1 & 6.6005.2) do so, but not the general 6.6002.1 Ducts, or 6.6002.2 Terminations (where one would expect it!). I was also very surprised at the requirement of R8 for ventilation (as compared to HVAC) duct insulation. [This actually pertains to the desired outcome for 6.6002.2 as a whole] | Accepted with Modifications | Change 6.6002.2f to include terminations to the outdoors" to align with range hood and dryer (6.6005.1 & 6.6005.2) | Change 6.6002.2f: Terminations will be ducted to the outdoors, which does not include unconditioned spaces such as attics and crawl spaces that are ventilated with the outdoors. Terminations will be installed: A minimum of 3' away from any property line A minimum of 3' away from operable opening to houses A minimum of 10' away from mechanical intake As required by authority having jurisdiction
Single-Family Homes | Ventilation | Exhaust | Fans | Through the Wall | Combustion safety | April 21, 2014 | April 21, 2014 | 6.6003.3k | An "excessively depressurized" CAZ with well-drafting appliances is considered acceptable. | Accepted with Modifications | SWS should be aligned with the latest codes and standards. | Pressure effects caused by fans will be assessed and corrected when found outside of combustion safety standards. Make-up air will be provided in accordance with the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction.
Single-Family Homes | Ventilation | Exhaust | Appliance Exhaust Vents | Clothes Dryer | Clothes dryer ducting | April 21, 2014 | April 21, 2014 | 6.6005.1a | Even though I'd prefer to see this section in Baseload, I don't mind it here. Really I think that the crawl-space and attic ventilation sections should all be in the Ventilation Section. | Rejected | Clothes dryers should be vented per the IRC and left in this section.
Single-Family Homes | Ventilation | Exhaust | Appliance Exhaust Vents | Clothes Dryer | Make-up air | April 21, 2014 | April 21, 2014 | 6.6005.1c | Should only be required if dryer is causing appliance to backdraft | Accepted with Modifications | SWS should be aligned with the latest codes and standards. | Make-up air will be provided in accordance with the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction for appliances exhausting more than 200 CFM
Single-Family Homes | Ventilation | Exhaust | Appliance Exhaust Vents | Clothes Dryer | Make-up air | April 21, 2014 | April 21, 2014 | 6.6005.1c | What is the expectation for this make up air? Is this to be made up by way of: air changes per hour, mechanically supplied, or combustion inlet tubes? The lack of information could lead to confusion. | Rejected | SWS was not intended to prescribe how to achieve the outcome.
Single-Family Homes | Ventilation | Exhaust | Appliance Exhaust Vents | Kitchen Range | Make-up air | April 21, 2014 | April 21, 2014 | 6.6005.2e | Should only be required if kitchen range fan is causing mechanicals to backdraft | Accepted with Modifications | SWS should be aligned with the latest codes and standards. | Make-up air will be provided in accordance with the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction for appliances exhausting more than 200 CFM
Single-Family Homes | Ventilation | Exhaust | Appliance Exhaust Vents | Kitchen Range | Make-up air | April 21, 2014 | April 21, 2014 | 6.6005.2e | What is the expectation for this make up air? Is this to be made up by way of: air changes per hour, mechanically supplied, or combustion inlet tubes? The lack of information could lead to confusion. | Rejected | SWS was not intended to prescribe how to achieve the outcome.
Multifamily Homes | Ventilation | Exhaust | Special Considerations | Regional Considerations | Very cold | April 10, 2014 | April 10, 2014 | 6.6088.1a | This comment is meant for the Detail level (as opposed to spec level). Rename the Detail "Regional Climatic Considerations...". "Regional Considerations" sounds like it could be any number of types of considerations, such as cultural, dialect, etc. | Accepted |  | Detail Title: Regional Climatic Considerations
Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens plus primary ventilation | April 21, 2014 | April 21, 2014 | 6.6201.1a | This is a comment on the whole section. Supply ventilation and exhaust ventilation are also whole-building ventilation, aren't they? If you don't include attic and crawl space ventilation in this section then the subtopics of the whole-building ventilation section are supply-only ventilation, exhaust-only ventilation, and balanced ventilation. What about a section on local ventilation where you discuss the local-ventilation requirements? | Accepted with Modifications | Topic will be renamed to "Whole-Building and Local Ventilation". Appendix A will be modified to be consistent with the most recent version of 62.2. | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See informative Appendix A for calculation information and examples.
Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens plus primary ventilation | April 18, 2014 | April 18, 2014 | 6.6201.1a | Change the word "intermittent" to "on-demand". This change was made in 62.2 to prevent confusion between fans that came on due to a scheduled control (intermittent) and fans that were on due to occupant decision (on-demand). | Accepted with Modifications | Topic will be renamed to "Whole-Building and Local Ventilation". Appendix A will be modified to be consistent with the most recent version of 62.2. | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See informative Appendix A for calculation information and examples.
Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens plus primary ventilation | April 18, 2014 | April 18, 2014 | 6.6201.1a | Change the 1 CFM to 3 CFM in the primary ventilation section, and refer to 62.2-2013. This suggested change is due to the release of ASHRAE 62.2-2013. | Accepted with Modifications | Topic will be renamed to "Whole-Building and Local Ventilation". Appendix A will be modified to be consistent with the most recent version of 62.2. | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See informative Appendix A for calculation information and examples.
Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens plus primary ventilation | April 11, 2014 | April 11, 2014 | 6.6201.1a | The continued use of ASHRAE 62.2 2010 (Or newer revisions) as a ventilation standard should seriously reconsidered. Under this ASRHAE standard we air-seal the home as tight as possible and then install a quiet, quality fan to provide a calculated minimum continuous flow of air into the living space. In a laboratory and on paper this standard looks like a good way to achieve proper ventilation in a home. In practical application, a weatherization client's home, it is a different matter entirely. These homes are not sterile laboratory facilities. These are real people who live in these homes. Often these homes are cluttered, dirty, and also house multiple pets. Fans running continuously, even in moderately clean homes collect dust and grime on the fan blades, housings and termination screens within months. Many of these clients are seniors, disabled or both and have no ability to perform this additional maintenance on their homes. Fans with built-in flow controls will try to make up for the loss of flow by increasing speed, but this will certainly hasten the death of the fan. Fans without built-in flow controls will gradually decrease in performance until its death too is hastened. This is not a not a theory but a observation of fans already installed under this ventilation standard by agencies across our state. Once these fans cease to function, which may after the 5 year warranty period of the fan, these clients will be left with tightly sealed homes with no way to deal with excess moisture or hazards from domestic pollutants in their homes. There is a high likelihood for this issue to occur in literally tens of thousands of homes across the United States. There is a huge risk in placing the entire burden of indoor air quality and indoor environmental hazard prevention on a mechanical device which can and will eventually fail. Please strongly consider removing this standard for a standard which relies on minimum ventilation levels and can be satisfied with passive ventilation measures. | Rejected | The ASHRAE Standard 62.2 is the accepted DOE standard.
Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens sufficient to meet primary ventilation requirements | April 18, 2014 | April 18, 2014 | 6.6201.1b | The second bullet under Kitchen should not be a bullet under Kitchen but rather a main item on its own. This is simply a formatting change, but as it stands it looks as though it only is part of the Kitchen section. | Accepted with Modifications | Topic will be renamed to "Whole-Building and Local Ventilation". Appendix A will be modified to be consistent with the most recent version of 62.2. | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See informative Appendix A for calculation information and examples.
Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens sufficient to meet primary ventilation requirements | April 18, 2014 | April 18, 2014 | 6.6201.1b | Change the 1 CFM to 3 CFM, and refer to 62.2-2013. This suggested change is due to the release of ASHRAE 62.2-2013. Update references to 62.2-2013. | Accepted with Modifications | Topic will be renamed to "Whole-Building and Local Ventilation". Appendix A will be modified to be consistent with the most recent version of 62.2. | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See informative Appendix A for calculation information and examples.
Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Single additional fan to meet all ventilation requirements | April 18, 2014 | April 18, 2014 | 6.6201.1c | Change the 1 CFM to 3 CFM, and refer to 62.2-2013. This suggested change is due to the release of ASHRAE 62.2-2013. Update references to 62.2-2013. | Accepted with Modifications | Topic will be renamed to "Whole-Building and Local Ventilation". Appendix A will be modified to be consistent with the most recent version of 62.2. | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See informative Appendix A for calculation information and examples.
Manufactured Housing | Ventilation | Whole Building Ventilation | Exhaust-Only System | Manufactured Housing Exhaust-Only Strategies | Location | April 21, 2014 | April 21, 2014 | 6.6205.1c | While I understand the goal of Ventilating common spaces, requiring the installation of a fan in a common area rather than a bathroom in a manufactured home will require: 1. A box to be built, as fans do not fit 6'' joists, 2. A new vent to be cut into a roof. 3. New wiring and switches to be installed by an electrician. The installed cost of this may easily exceed $1,000.00, and this is not in my opinion acceptable for the cost vs benefits. | Accepted | There is no difference between a bathroom in a mobile home or single or multifamily. | Eliminate entire section.
Single-Family Homes | Ventilation | Whole Building Ventilation | Special Considerations | Sound-Rating Limits | Primary ventilation system or any continuously operating fan | April 1, 2013 | March 12, 2014 | 6.6288.1a | In 6.6288.1a, Primary ventilation, and 1b, Intermittent local ventilation, list ASHRAE sone requirements of 1 and 3, but fail to point out that these standards apply ONLY to NEW installed equipment. | Accepted with Modifications | System shall be rated for sound in accordance with current ASHRAE 62.2 standard. | System shall be rated for sound at a maximum of 1.0 sone, in accordance with current ASHRAE 62.2-2010 standard
Multifamily Homes | Ventilation | Whole Building Ventilation | Special Considerations | Regional Considerations | Very cold | April 10, 2014 | April 10, 2014 | 6.6288.3a | This comment is meant for the Detail level (as opposed to spec level). Rename the Detail "Regional Climatic Considerations...". "Regional Considerations" sounds like it could be any number of types of considerations, such as cultural, dialect, etc. | Accepted |  | Detail Title: Regional Climatic Considerations
Single-Family Homes | Baseload | Plug Load | Refrigerators/Freezers | Refrigerator and Freezer Replacement | Selection | February 21, 2014 | February 21, 2014 | 7.8001.1a | Desired outcome should be similar to 7.8001.3a: "Energy efficient appliance installed". | Accepted |  | The Desired Outcome for 7.8001.3 should read, "Energy efficient appliance installed."
Multifamily Homes | Baseload | Plug Load | Lighting | Bi-Level Controls | Installation | April 18, 2014 | April 18, 2014 | 7.8003.10c | Installation shall meet state code requirements where applicable | Rejected | Although the document is inconsistent with its wording, this information is already reflected within the SWS.
Single-Family Homes | Baseload | Plug Load | Lighting | Lighting Upgrade | Selection | April 6, 2014 | April 6, 2014 | 7.8003.1b | This is one of those sections that I can't quite believe that agencies are going to do all this stuff in the execution of the standard. For example, power quality? We're going go bust out our oscilloscopes and start evaluating wave forms? What does power quality have to do with residential energy conservation and what would we do about bad harmonics if we found them? | Accepted |  | Delete "Power quality will be evaluated before new lighting is selected"
Single-Family Homes | Baseload | Plug Load | Lighting | Lighting Upgrade | Selection | April 21, 2014 | April 21, 2014 | 7.8003.1b | Lighting control and other technologies would have to be cost justified. | Rejected | These specifications are not just for the weatherization network. They apply to the entire home performance industry; cost-effectiveness is not always the most important factor - sometimes comfort is the priority.
Single-Family Homes | Baseload | Plug Load | Lighting | Lighting Upgrade | Selection | April 7, 2014 | April 7, 2014 | 7.8003.1b | So is this standard saying that a dimmer is a cost-effective ECM? | Rejected | These specifications are not just for the weatherization network, they apply to the entire home performance industry; cost-effectiveness is not always the most important factor - sometimes comfort is the priority.
Multifamily Homes | Baseload | Plug Load | Lighting | Occupancy Sensors for Indoor Common Areas and Offices | Installation | April 18, 2014 | April 18, 2014 | 7.8003.6c | Installation to meet state code where applicable. | Rejected | Although the document is inconsistent with its wording, this information is already reflected within the SWS.
Multifamily Homes | Baseload | Plug Load | Lighting | Stand-Alone Timers in Outdoor and Common Areas | Installation | April 18, 2014 | April 18, 2014 | 7.8003.7c | installation shall meet state code requirements where applicable. | Rejected | Although the document is inconsistent with its wording, this information is already reflected within the SWS.
Single-Family Homes | Baseload | Plug Load | Laundry | Clothes Dryer Replacement | Installation | April 21, 2014 | April 21, 2014 | 7.8004.2b | Lint-plugged dryer vents are an energy waster and a fire hazard. We have information on dryer venting in the Ventilation section. Why not move it here, and talk also about dryer maintenance and re-venting if necessary? | Accepted with Modifications | The committee agrees that the specification needs to be modified to add language: Venting will not be constricted or blocked | Add "and should be free of lint and/or debris"
Single-Family Homes | Baseload | Plug Load | Laundry | Clothes Dryer Replacement | Installation | April 6, 2014 | April 6, 2014 | 7.8004.2b | How do you use screws to join vent together and ensure that they won't collect lint? | Accepted with Modifications | The industry best practice is to employ mechanical fasteners; the commenter is correct that screws would catch lint. | Must be mechanically fastened to connect metal-to-metal and must not catch lint inside venting material.
Multifamily Homes | Baseload | Plug Load | Laundry | Clothes Dryer Replacement | Installation | April 18, 2014 | April 18, 2014 | 7.8004.3c | What about design consideration for demand control exhaust ventilation | Accepted |  | Venting design will meet standards for optimal venting, including demand control venting.
Multifamily Homes | Baseload | Water Heating | Water Use Reduction | Low-Flow Retrofit Devices | Removal | April 18, 2014 | April 18, 2014 | 7.8101.2a | With the shower on, evaluation of water diverter for leaking should be done. | Rejected | Evaluation and repair would be cost prohibitive. If further water savings are required, see EPA Water Sense.
Multifamily Homes | Baseload | Water Heating | Water Use Reduction | Low-Flow Retrofit Devices | Installation | April 18, 2014 | April 18, 2014 | 7.8101.2b | what is the reason behind no shutoff valves on showerheads in a central DHW system?. there is a showerhead shutoff product that shuts the flow off to the shower when temp is met. It works with a central DHW system. | Accepted | Our experience is that shutoff valves for showerheads, e.g. temperature-protected, Evolve, have worked to save energy and reduce water waste. Please note: We are assuming this is in reference to a temperature controlled shutoff valve, and not manual. | Low-flow showerheads or aerators will be installed using a non-hardening thread sealant Temperature-protected shutoff valves will be used Showerheads with shut off valves will not be installed in buildings with central water heating systems
Single-Family Homes | Baseload | Water Heating | Installation and Replacement | Water Heater Selection | Selection parameters | January 30, 2013 | March 12, 2014 | 7.8102.1a | Iowa is working on the Weatherization Standards/Field Guides for our sub-grantees. The SWS (Section 7.8102.1) requires Energy Star rating direct vent for combustion water heaters for manufactured homes. We are having trouble finding an Energy Star water heater that is rated by HUD for manufactured housing and mobile homes. Do you know where we can find water heaters that meet SWS requirements for mobile homes? [This actually pertains to the desired outcome for 7.8102. as a whole] This comment was submitted by Gwen Howe, however I am not sure if he has a user account. | Accepted |  | If a combustion-based system is selected, it will be either direct vented or power vented, and ENERGY STAR qualified or an Energy Factor (EF) of .58 or higher.
Single-Family Homes | Baseload | Water Heating | Installation and Replacement | Storage-Type Appliance | Emergency drain pan | April 7, 2014 | April 7, 2014 | 7.8102.2d | Drain pans usually sit on the floor and are 1.5 to 2 inches high. The code says not less than 1.5 inches. | Rejected | Specification exceeds code to better protect the consumer.
Single-Family Homes | Baseload | Water Heating | Installation and Replacement | Storage-Type Appliance | Occupant safety | April 21, 2014 | April 21, 2014 | 7.8102.2m | Please clarify specification to provide list of monitors that provide more detail on CO levels; all electric dwellings without attached garage do not need CO | Rejected | We agree with ASHRAE 62.2-2013 that states a CO alarm is required in all dwellings.
Single-Family Homes | Baseload | Water Heating | Installation and Replacement | On-Demand Appliance | Required combustion air | April 7, 2014 | April 7, 2014 | 7.8102.3i | I don't understand why the combustion-air requirements and combustion testing requirements are present for the On-Demand unit and not for the storage unit. | Accepted |  | Electric or fossil fuel supply components will be installed to accepted industry standards as per Chapter 24 of the 2012 IRC , NFGC and NFPA 31 and 54 for gas and oil, or NEC for electric Energy input required by the appliance will be in accordance with manufacturer specifications All on-demand appliances will be installed per manufacturer recommendations/specifications.
Single-Family Homes | Baseload | Water Heating | Maintenance/Inspection | Storage-Type Appliance | Health and safety | April 7, 2014 | April 7, 2014 | 7.8103.1a | This is a comment on the naming of the bold numbered headlines. These headings should be more specific. For example: Storage Water Heater Maintenance or Storage Water Heater Replacement. Right now you have a number of headings that are the same and this is confusing. | Rejected | Existing SWS nomenclature is consistent and logical.
Single-Family Homes | Baseload | Water Heating | Maintenance/Inspection | Storage-Type Appliance | Thermal efficiency | April 21, 2014 | April 21, 2014 | 7.8103.1c | If the water heater has Energy Star rating, why would a minimum R-value of 24 be needed? This is 2-3 times the typicall Energy Star model actual level. | Accepted with Modifications | R-24 could be a little too much for certain climates (i.e. conditioned/unconditioned space) | Water heater storage tanks shall have a minimum R-value of R-24, unless the SIR to add insulation is less than 1.0 Added insulation will not obstruct the unit's draft diverter, pressure relief valve, thermostats, hi-limit switch , plumbing pipes or elements, and thermostat access plates The first 6' of inlet and outlet piping will be insulated in accordance with 2012 IRC N1103.4.2 or local requirements, whichever is greater
Single-Family Homes | Baseload | Water Heating | Maintenance/Inspection | Storage-Type Appliance | Occupant safety | April 21, 2014 | April 21, 2014 | 7.8103.1g | Please clarify specification to provide list of monitors that provide more detail on CO levels; all electric dwellings without attached garage do not need CO | Rejected | We agree with ASHRAE 62.2-2013 that states a CO alarm is required in all dwellings.
Multifamily Homes | Baseload | Water Heating | Maintenance/Inspection | Operation Manual | Content | April 18, 2014 | April 18, 2014 | 7.8103.6b | Ensure DHW storage tanks are maintained at min 130 degrees to prevent occurrence of Legionella. Tempering reducing valve setting will be maintained to lowest possible/allowable dhw temp | Rejected | The specification does not specify a temperature. The industry accepted value is setting the water heater to a temperature of 120F.
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.1d | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.3c | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.4d | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.8 | Committee changes in response to comment on 4.1005.2d | Accepted |  | need to add “g” row to meet the CFR requirement, language below works. Title can be "Onsite Documentation” and Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.9 | Committee changes in response to comment on 4.1005.2d | Accepted |  | need to add “g” row to meet the CFR requirement, language below works. Title can be "Onsite Documentation” and Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.10 | Committee changes in response to comment on 4.1005.2d | Accepted |  | need to add “h” row to meet the CFR requirement, language below works. Title can be "Onsite Documentation” and Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.11 | Committee changes in response to comment on 4.1005.2d | Accepted |  | need to add “b” row to meet the CFR requirement, language below works. Title can be "Onsite Documentation” and Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.14g | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1005.2d | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1005.4d | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1005.8d | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.2d | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.3d | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.7d | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.13d | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1303.1e | Committee changes in response to comment on 4.1005.2d | Accepted |  | Update specification column to read: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and minimum settled thickness • Number of bags installed in accordance with manufacturer specifications Update Objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.2 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add a “b” row to meet the CFR requirement, language below works. Title can be "Onsite Documentation” and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.5b | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.6b | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.12 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add “g” row to meet the CFR requirement, language below works. Title can be "Onsite Documentation” and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1003.13b | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1004.4d | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1004.5 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1005.1c | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1005.3c | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1005.5d | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1005.6c | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1005.7d | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1006.1d | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1006.2e | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1088.4 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1088.5 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1102.2 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1103.1 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1103.2 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1103.3d | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1103.4 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1104.1 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1104.2 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1104.3 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1104.4 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.1d | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.4d | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.5e | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.6e | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.8d | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.9 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.11e | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.12 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.14j | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.15h | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1303.2e | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1303.3g | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1401.1 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1402.1 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1402 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1402.3 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1403.1j | Committee changes in response to comment on 4.1005.2d | Accepted |  | and Update the specification column to read: A dated receipt signed by the installer will be provided that includes: • Coverage area • Thickness • R-value Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1002.2c | Committee changes in response to comment on 4.1005.2d | Accepted |  | Use this language in spec: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and settled thickness (settled thickness required for loose-fill only) • Number of bags installed in accordance with manufacturer specifications (for loose-fill only) Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1088.3c | Committee changes in response to comment on 4.1005.2d | Accepted |  | Use this language in spec: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and settled thickness (settled thickness required for loose-fill only) • Number of bags installed in accordance with manufacturer specifications (for loose-fill only) Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1088.6 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and use this language in spec: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and settled thickness (settled thickness required for loose-fill only) • Number of bags installed in accordance with manufacturer specifications (for loose-fill only) Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1102.1d | Committee changes in response to comment on 4.1005.2d | Accepted |  | Use this language in spec: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and settled thickness (settled thickness required for loose-fill only) • Number of bags installed in accordance with manufacturer specifications (for loose-fill only) Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1103.5 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to add row and use this language in spec: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and settled thickness (settled thickness required for loose-fill only) • Number of bags installed in accordance with manufacturer specifications (for loose-fill only) Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1301.1k | Committee changes in response to comment on 4.1005.2d | Accepted |  | Use this language in spec: A dated receipt signed by the installer will be provided that includes: • Insulation type • Coverage area • R-value • Installed thickness and settled thickness (settled thickness required for loose-fill only) • Number of bags installed in accordance with manufacturer specifications (for loose-fill only) Update the objective(s) column to read: Document job completion to contract specifications Confirm amount of insulation installed Comply with 16 CFR 460.17
| Insulation |  |  |  |  | April 21, 2014 | April 21, 2014 | 4.1088.2 | Committee changes in response to comment on 4.1005.2d | Accepted |  | Need to row titled "Onsite Documentation" and Use this language in spec: A dated receipt signed by the installer will be provided that includes: • Number and thickness of air spaces • R-value • Direction of heat flow Update the objective(s) column to read: Document job completion to contract specifications Comply with 16 CFR 460.17

## Adjudication (hidden)
Adjudication
Accepted
Accepted with Modifications
Further Investigation Required
Rejected

## Data (hidden)
[6 empty] | Row Labels | Count of Submitted By
Count of Submitted By | Column Labels |  |  |  |  | Combustion Safety | 35
Row Labels | Accepted | Accepted with Modifications | Further Investigation Required | Rejected | Grand Total | Attics (Air Sealing & Insulation) | 31
Air Sealing | 10 |  |  | 9 | 19 | Moisture | 26
Baseload | 6 | 3 |  | 11 | 20 | Safe Work Practices | 12
Health and Safety | 12 | 16 | 15 | 42 | 85 | Exhaust | 10
Heating and Cooling | 2 | 2 | 1 | 2 | 7 | Plug Load | 10
Insulation | 18 | 3 | 3 | 12 | 36 | Water Heating | 10
Ventilation | 3 | 12 |  | 5 | 20 | Whole Building Ventilation | 10
Grand Total | 51 | 36 | 19 | 81 | 187 | Ducts | 8
[6 empty] | Occupant Education and Access | 7
[6 empty] | Basements and Crawl Spaces | 5
[6 empty] | Forced Air | 5
|  |  |  | Row Labels | Count of Submitted By
|  |  | Air Sealing | Attics | 7
|  |  |  | Basements and Crawl Spaces | 4
|  |  |  | Ducts | 6
|  |  |  | Windows and Doors | 2
|  |  | Baseload | Plug Load | 10
|  |  |  | Water Heating | 10
|  |  | Health and Safety | Combustion Safety | 35
|  |  |  | Electrical | 1
|  |  |  | Moisture | 26
|  |  |  | Occupant Education and Access | 7
|  |  |  | Radon | 2
|  |  |  | Safe Work Practices | 12
|  |  |  | Safety Devices | 2
|  |  | Heating and Cooling | Forced Air | 5
|  |  |  | Hydronic Heating (Hot Water and Steam) | 1
|  |  |  | Shading | 1
|  |  | Insulation | Access Doors and Hatches | 1
|  |  |  | Attics | 24
|  |  |  | Basements and Crawl Spaces | 1
|  |  |  | Ducts | 2
|  |  |  | Fireplace Chimney and Combustion Flue Vents | 1
|  |  |  | Floors | 2
|  |  |  | Non-Insulation Contact (IC) Recessed Light | 1
|  |  |  | Pitched/Vaulted/Cathedralized Ceilings—Dense Pack Over | 1
|  |  |  | Unvented Roof Deck—Preparation for Spray Polyurethane Foam | 1
|  |  |  | Walls | 2
|  |  | Ventilation | Exhaust | 10
|  |  |  | Whole Building Ventilation | 10